## Index
Catalogue Index
No. | Worksheet
1 | Intro
2 | alldata_long
3 | Notes
4 | Ref
5 | 01 Coal CHP
6 | 02 LTE existing plant
7 | 03a Coal to wood pellets exi bo
8 | 03b Coal to wood chips n. boile
9 | 03c coal to wood chips exi. boi
10 | 03d coal to wood chips exi. boi
11 | 04 Gas turb. simple cycle, L
12 | 04 Gas turb. simple cycle Sm-Me
13 | 04 Gas turb. simple cycle Micro
14 | 05 Gas turb. CC, steam extract.
15 | 05 Gas turb. CC, Back-pressure
16 | 06 Gas engines, natural gas
17 | 06 Gas engines, biogas
18 | 08 WtE CHP, Large, 40 degree
19 | 08 WtE CHP, Large, 50 degree
20 | 08 WtE CHP, Medium
21 | 08 WtE CHP, Small
22 | 08 WtE HOP
23 | 09a Wood Chips, Large 40 degree
24 | 09a Wood Chips, Large 50 degree
25 | 09a Wood Chips, Medium
26 | 09a Wood Chips, Small
27 | 09b Wood Pellets, Large 40 degr
28 | 09b Wood Pellets, Large 50 degr
29 | 09b Wood Pellets, Medium
30 | 09b Wood Pellets, Small
31 | 09c Straw, Large, 40 degree
32 | 09c Straw, Large, 50 degree
33 | 09c Straw, Medium
34 | 09c Straw, Small
35 | 09a Wood Chips HOP, small
36 | 09a Wood Chips HOP, medium
37 | 09a Wood Chips HOP, large
38 | 09b Wood Pellets HOP
39 | 09c Straw HOP
40 | 09a Wood Chips extract. plant
41 | 09b Wood Pellets extract. plant
42 | 10 Stirling
43 | 11 SOFC-CHP
44 | 12 LT-PEMFC CHP
45 | 20 Onshore turbines
46 | 20 Domestic turbines
47 | 21 Nearshore Wind AC
48 | 21 Offshore Wind AC Fixed
49 | 21 Offshore Wind AC Floating
50 | 21 Far shore Wind DC Fixed
51 | 21 Far shore Wind DC Floating
52 | 22 Rooftop PV residential
53 | 22 Rooftop PV comm.&industrial
54 | 22 Utility-scale PV tracker
55 | 22 Utility-scale PV
56 | 22 Rooftop resid PV+BESS co-loc
57 | 22 Rooftop com indu PV+BESS co
58 | 22 Utility-scale PV+BESS co-lo
59 | 23 Wave Energy
60 | 40 Comp. hp, airsource 1 MW
61 | 40 Comp. hp, airsource 3 MW
62 | 40 Comp. hp, airsource 10 MW
63 | 40 Comp. hp, waste heat 1 MW
64 | 40 Comp. hp, waste heat 3 MW
65 | 40 Comp. hp, waste heat 10 MW
66 | 40 Comp. hp, seawater 20 MW
67 | 40 Comp. hp, seawater 50-100 MW
68 | 41 Electric boiler, small
69 | 41 Electric boiler, large
70 | 44 Natural Gas DH Only
71 | 45.1.a Geothermal DH, 1200m
72 | 45.1.b Geothermal DH, 2000m
73 | 45.2.a Geothermal DH, LT, 1200m
74 | 45.2.b Geothermal DH, LT, 2000m
75 | 45.3 Geothermal DH, lar scale
76 | 46 Solar District Heating
77 | 47 Oil DH Only
78 | 50 Diesel engine farm
79 | 51 Natural gas engine plant
80 | 52 OCGT - Natural gas
81 | 52 OCGT - Light fuel oil
Refresh Index

## Intro
Back to Index
Technology Data for power and heat production plants
| Version | 0019
This file contains technology data sheets related to generation of electricity and district heating. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found.
Dates and descriptions of updates are listed in the ammendment sheet below.
Additional information about the syntax of parameters and units in the datatabels is listed below.
Parameter structure: parameter name (extra info) [unit]. For financial parameters priceyear is expressed as: [priceyear-unit]
Subscript abbreviations used in the datasheets: input = _i, electricity production/consumption = _e, heat production/consumption = _h
The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
The sheet alldata_flat contains all technology data in this catalogue in a flat format.
| Cost data is in | 2020 | EURO
| Cost data for datasheets 22x, 40x, 41x, 45x and 47x is in 2025 |  | EURO (specified in the specific datasheets)
License:
This work is licensed under Attribution 4.0 International
Ammendment sheet
| Date | Sheet | Change | Notes
| 2026-08-26 | 22 Solar PV | Update assumptions and add co-located storage systems
| 2026-01-14 | 23 Wave Energy | Datasheet removed
| 2026-01-14 | 40 Heat pumps | All datasheets updated. Datasheet on absorption heat pump removed
| 2026-01-14 | 41 Electric boilers | Datasheets updated
| 2026-01-14 | 42 Oil boiler | New datasheet added
| 2026-01-14 | 45 Geothermal | All datasheets updated. 2 datasheets with absorption heat pumps removed
| 2025-02-03 | 21 Offshore turbines | Datasheets updated and extended to in total five datasheets
| 2024-02-24 | 20 Onshore turbines | Datasheets updated
| 2023-08-23 | all sheets | Update to 2020 prices
| 2022-06-01 | 40 Heat pumps | Addition of datasheet about CO2 heat pumps
| 2022-06-01 | 45 Geothermal | Addition of datasheet about large scale geothermal with electric heat pump
| mar-22 | 21 Offshore and near shore turbines | Offshore and Nearshore turbines updated. Financial data now in 2020€.
| feb-22 | 22 Photovoltaics | All datasheets for PV systems updated. Financial data now in 2020€.
| apr-20 | 40 Heat pumps | Compression heat pumps (electric) updated. Datasheets now divided in 3 types and different plant sizes.
| apr-20 | 45 Geothermal | Datasheets updated and now divided in 1200 m and 2000 m depth, electric- and absorption heat pumps and 2 different district heating temperatures.
| mar-20 | 09a medium and large biomass HOP | Added datasheets of medium and large biomass HOP
| mar-20 | 09 Biomass plants | Minor update of existing biomass datasheets
| jan-20 | 09 Biomass plants | Datasheets updated
| nov-19 | 22 Photovoltaics Large | Updated data sheet for large utility scale PV systems
| nov-19 | 22 Photovoltaics Tracker | New data sheet for large utility scale PV systems with single axis tracker
| sep-19 | 21 Near shore turbines | Minor adjustment
| jun-19 | 03 Rebuilding large coal power plants to biomass | Added Datasheet d for rebuild coal fired plants to chips backpressure plant. Updated datasheets a and b for rebuild coal fired plants to wood pellets
| maj-19 | 20 Wind turbines, on-shore | Onshore and domestic turbines updated
| maj-19 | 21 Offshore and near shore turbines | Offshore and nearshore tubrines updated
| nov-18 | 50-52 peak plants | Datasheets added for diesel engine farms, natural gas engine plant and open cycle gas turbines.
| okt-18 | 46 Solar District Heating | Update
| mar-18 | 08 WtE plants | Datasheets added
| jan-18 | 04, 05 and 06 gas turbines and engines
| jan-18 | 11 Solid oxide fuel cell (SOFC) CHP, natural gas/biogas | Datasheets added
| jan-18 | 12 Low temperature proton exchange membrane fuel cell (LT-PEMFC) CHP, hydrogen
| jan-18 | 41 Electric Boiler | Update
| jan-18 | 44 District heating boilers, Gas fired | Update
| nov-17 | 01 Supercritical Pulverized Fuel Power Plant - Coal CHP

## alldata_long
Back to Index
catalogue_key | ws | technology | cat | par | unit | priceyear | note | ref | est | year | val | technology_key | cat_key | par_key | technology_id | cat_id | cat_id_source | par_id
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | A |  | ctrl | 2015 | 0.75 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0020 | tk_etd | manual_category_map | PAR_0015
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | A |  | ctrl | 2020 | 0.84 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0020 | tk_etd | manual_category_map | PAR_0015
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | A |  | ctrl | 2030 | 1.01 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0020 | tk_etd | manual_category_map | PAR_0015
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Construction time [years] | years |  |  | [2, 3, 3] | ctrl | 2015 | 4.5 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | construction time [years] | ELH_0020 | tk_etd | manual_category_map | PAR_0026
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Construction time [years] | years |  |  | [2, 3, 3] | ctrl | 2020 | 4.5 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | construction time [years] | ELH_0020 | tk_etd | manual_category_map | PAR_0026
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Construction time [years] | years |  |  | [2, 3, 3] | ctrl | 2030 | 4.5 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | construction time [years] | ELH_0020 | tk_etd | manual_category_map | PAR_0026
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  | 1 | ctrl | 2015 | 0.15 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | cv coefficient (50°c/100°c) | ELH_0020 | tk_etd | manual_category_map | PAR_0028
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  | 1 | ctrl | 2020 | 0.15 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | cv coefficient (50°c/100°c) | ELH_0020 | tk_etd | manual_category_map | PAR_0028
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  | 1 | ctrl | 2030 | 0.15 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | cv coefficient (50°c/100°c) | ELH_0020 | tk_etd | manual_category_map | PAR_0028
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | [8, 7, 9, 11] | ctrl | 2015 | 0.46 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0020 | tk_etd | manual_category_map | PAR_0036
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | [8, 7, 9, 11] | ctrl | 2020 | 0.485 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0020 | tk_etd | manual_category_map | PAR_0036
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | [8, 7, 9, 11] | ctrl | 2030 | 0.52 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0020 | tk_etd | manual_category_map | PAR_0036
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | [8, 7, 9, 11] | ctrl | 2050 | 0.535 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0020 | tk_etd | manual_category_map | PAR_0036
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 500 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0020 | tk_etd | manual_category_map | PAR_0071
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 500 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0020 | tk_etd | manual_category_map | PAR_0071
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 500 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0020 | tk_etd | manual_category_map | PAR_0071
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2050 | 500 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0020 | tk_etd | manual_category_map | PAR_0071
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 6 | ctrl | 2015 | 25 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | technical lifetime [years] | ELH_0020 | tk_etd | manual_category_map | PAR_0198
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 6 | ctrl | 2020 | 25 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | technical lifetime [years] | ELH_0020 | tk_etd | manual_category_map | PAR_0198
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 6 | ctrl | 2030 | 25 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | technical lifetime [years] | ELH_0020 | tk_etd | manual_category_map | PAR_0198
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 6 | ctrl | 2050 | 25 | coal power plant, supercritical - extraction - coal - medium | energy/technical data | technical lifetime [years] | ELH_0020 | tk_etd | manual_category_map | PAR_0198
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2015 | 1.5 | coal power plant, supercritical - extraction - coal - medium | environment | ch4 [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0018
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2020 | 1.5 | coal power plant, supercritical - extraction - coal - medium | environment | ch4 [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0018
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2030 | 1.5 | coal power plant, supercritical - extraction - coal - medium | environment | ch4 [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0018
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2050 | 1.5 | coal power plant, supercritical - extraction - coal - medium | environment | ch4 [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0018
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2015 | 0.8 | coal power plant, supercritical - extraction - coal - medium | environment | n2o [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0089
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2020 | 0.8 | coal power plant, supercritical - extraction - coal - medium | environment | n2o [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0089
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2030 | 0.8 | coal power plant, supercritical - extraction - coal - medium | environment | n2o [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0089
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2050 | 0.8 | coal power plant, supercritical - extraction - coal - medium | environment | n2o [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0089
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2015 | 38 | coal power plant, supercritical - extraction - coal - medium | environment | nox [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0152
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2020 | 35 | coal power plant, supercritical - extraction - coal - medium | environment | nox [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0152
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2030 | 35 | coal power plant, supercritical - extraction - coal - medium | environment | nox [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0152
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2050 | 35 | coal power plant, supercritical - extraction - coal - medium | environment | nox [g/gj_i] | ELH_0020 | tk_env | manual_category_map | PAR_0152
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | SO2 (degree of desulphuring) [] |  |  | B | 5 | ctrl | 2015 | 0.97 | coal power plant, supercritical - extraction - coal - medium | environment | so2 (degree of desulphuring) [] | ELH_0020 | tk_env | manual_category_map | PAR_0181
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | SO2 (degree of desulphuring) [] |  |  | B | 5 | ctrl | 2020 | 0.97 | coal power plant, supercritical - extraction - coal - medium | environment | so2 (degree of desulphuring) [] | ELH_0020 | tk_env | manual_category_map | PAR_0181
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | SO2 (degree of desulphuring) [] |  |  | B | 5 | ctrl | 2030 | 0.97 | coal power plant, supercritical - extraction - coal - medium | environment | so2 (degree of desulphuring) [] | ELH_0020 | tk_env | manual_category_map | PAR_0181
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | SO2 (degree of desulphuring) [] |  |  | B | 5 | ctrl | 2050 | 0.97 | coal power plant, supercritical - extraction - coal - medium | environment | so2 (degree of desulphuring) [] | ELH_0020 | tk_env | manual_category_map | PAR_0181
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 35618.9884 | coal power plant, supercritical - extraction - coal - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0020 | tk_fin | manual_category_map | PAR_0042
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 35053.6077 | coal power plant, supercritical - extraction - coal - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0020 | tk_fin | manual_category_map | PAR_0042
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 34324.4022 | coal power plant, supercritical - extraction - coal - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0020 | tk_fin | manual_category_map | PAR_0042
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 32911.1764 | coal power plant, supercritical - extraction - coal - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0020 | tk_fin | manual_category_map | PAR_0042
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 2.1824 | coal power plant, supercritical - extraction - coal - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0020 | tk_fin | manual_category_map | PAR_0093
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 2.1484 | coal power plant, supercritical - extraction - coal - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0020 | tk_fin | manual_category_map | PAR_0093
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 2.1032 | coal power plant, supercritical - extraction - coal - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0020 | tk_fin | manual_category_map | PAR_0093
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 2.0128 | coal power plant, supercritical - extraction - coal - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0020 | tk_fin | manual_category_map | PAR_0093
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 3.3357 | coal power plant, supercritical - extraction - coal - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0020 | tk_fin | manual_category_map | PAR_0201
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 3.2792 | coal power plant, supercritical - extraction - coal - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0020 | tk_fin | manual_category_map | PAR_0201
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 3.2114 | coal power plant, supercritical - extraction - coal - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0020 | tk_fin | manual_category_map | PAR_0201
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 3.0757 | coal power plant, supercritical - extraction - coal - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0020 | tk_fin | manual_category_map | PAR_0201
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | [10, 14] | ctrl | 2015 | 0.18 | coal power plant, supercritical - extraction - coal - medium | regulation ability | minimum load (of full load) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0085
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | [10, 14] | ctrl | 2020 | 0.15 | coal power plant, supercritical - extraction - coal - medium | regulation ability | minimum load (of full load) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0085
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | [10, 14] | ctrl | 2030 | 0.15 | coal power plant, supercritical - extraction - coal - medium | regulation ability | minimum load (of full load) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0085
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | [10, 14] | ctrl | 2050 | 0.1 | coal power plant, supercritical - extraction - coal - medium | regulation ability | minimum load (of full load) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0085
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | D | 14 | ctrl | 2015 | 0.05 | coal power plant, supercritical - extraction - coal - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0171
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | D | 14 | ctrl | 2020 | 0.05 | coal power plant, supercritical - extraction - coal - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0171
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | D | 14 | ctrl | 2030 | 0.05 | coal power plant, supercritical - extraction - coal - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0171
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | D | 14 | ctrl | 2050 | 0.05 | coal power plant, supercritical - extraction - coal - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0171
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 14 | ctrl | 2015 | 0.04 | coal power plant, supercritical - extraction - coal - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0179
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 14 | ctrl | 2020 | 0.04 | coal power plant, supercritical - extraction - coal - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0179
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 14 | ctrl | 2030 | 0.04 | coal power plant, supercritical - extraction - coal - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0179
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 14 | ctrl | 2050 | 0.04 | coal power plant, supercritical - extraction - coal - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0020 | tk_reg | manual_category_map | PAR_0179
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Technology-specific data | Availability [] |  |  | E | 7 | ctrl | 2015 | 0.95 | coal power plant, supercritical - extraction - coal - medium | technology-specific data | availability [] | ELH_0020 | tk_tsd | manual_category_map | PAR_0007
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Technology-specific data | Availability [] |  |  | E | 7 | ctrl | 2020 | 0.95 | coal power plant, supercritical - extraction - coal - medium | technology-specific data | availability [] | ELH_0020 | tk_tsd | manual_category_map | PAR_0007
ELH | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Technology-specific data | Availability [] |  |  | E | 7 | ctrl | 2030 | 0.95 | coal power plant, supercritical - extraction - coal - medium | technology-specific data | availability [] | ELH_0020 | tk_tsd | manual_category_map | PAR_0007
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0016
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0016
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0016
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0016
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0016
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Construction time [years] | years |  |  | 7 | ctrl | 2015 | 0.5 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | construction time [years] | ELH_0049 | tk_etd | manual_category_map | PAR_0026
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Construction time [years] | years |  |  | 7 | ctrl | 2020 | 0.5 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | construction time [years] | ELH_0049 | tk_etd | manual_category_map | PAR_0026
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Construction time [years] | years |  |  | 7 | ctrl | 2030 | 0.5 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | construction time [years] | ELH_0049 | tk_etd | manual_category_map | PAR_0026
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0029
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0029
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0029
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0029
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0049 | tk_etd | manual_category_map | PAR_0029
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0035
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0035
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0035
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | lower | 2020 | -0.01 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0035
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | upper | 2020 | 0.01 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0035
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0037
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0037
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0037
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | lower | 2020 | -0.01 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0037
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | upper | 2020 | 0.01 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0037
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0063
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0063
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0063
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0063
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0049 | tk_etd | manual_category_map | PAR_0063
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 300 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0071
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 300 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0071
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 300 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0071
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 200 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0071
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 200 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0071
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 400 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0071
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 400 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0071
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0049 | tk_etd | manual_category_map | PAR_0166
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0049 | tk_etd | manual_category_map | PAR_0166
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0049 | tk_etd | manual_category_map | PAR_0166
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0049 | tk_etd | manual_category_map | PAR_0166
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0049 | tk_etd | manual_category_map | PAR_0166
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0185
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0185
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0185
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0185
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0049 | tk_etd | manual_category_map | PAR_0185
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Technical lifetime [years] | years |  |  | [4, 5, 6, 7] | ctrl | 2015 | 15 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | technical lifetime [years] | ELH_0049 | tk_etd | manual_category_map | PAR_0198
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Technical lifetime [years] | years |  |  | [4, 5, 6, 7] | ctrl | 2020 | 15 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | technical lifetime [years] | ELH_0049 | tk_etd | manual_category_map | PAR_0198
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Technical lifetime [years] | years |  |  | [4, 5, 6, 7] | ctrl | 2030 | 15 | life time extension of coal extraction plant - refurbish - coal - large | energy/technical data | technical lifetime [years] | ELH_0049 | tk_etd | manual_category_map | PAR_0198
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | ch4 (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0017
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | ch4 (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0017
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | ch4 (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0017
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | ch4 (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0017
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | ch4 (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0017
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | n2o (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0088
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | n2o (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0088
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | n2o (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0088
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | n2o (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0088
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | n2o (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0088
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | nox (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0151
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | nox (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0151
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | nox (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0151
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | nox (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0151
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | nox (additional to existing plant) [g/gj_i] | ELH_0049 | tk_env | manual_category_map | PAR_0151
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | so2 (degree of desulphuring, additional to existing plant) [] | ELH_0049 | tk_env | manual_category_map | PAR_0182
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | so2 (degree of desulphuring, additional to existing plant) [] | ELH_0049 | tk_env | manual_category_map | PAR_0182
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | so2 (degree of desulphuring, additional to existing plant) [] | ELH_0049 | tk_env | manual_category_map | PAR_0182
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | so2 (degree of desulphuring, additional to existing plant) [] | ELH_0049 | tk_env | manual_category_map | PAR_0182
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | environment | so2 (degree of desulphuring, additional to existing plant) [] | ELH_0049 | tk_env | manual_category_map | PAR_0182
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0049 | tk_fin | manual_category_map | PAR_0048
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0049 | tk_fin | manual_category_map | PAR_0048
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0049 | tk_fin | manual_category_map | PAR_0048
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | ctrl | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0049 | tk_fin | manual_category_map | PAR_0048
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0049 | tk_fin | manual_category_map | PAR_0048
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | lower | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0049 | tk_fin | manual_category_map | PAR_0048
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | upper | 2020 | 8506.9817 | life time extension of coal extraction plant - refurbish - coal - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0049 | tk_fin | manual_category_map | PAR_0048
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | upper | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0049 | tk_fin | manual_category_map | PAR_0048
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | ctrl | 2015 | 0.25521 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0093
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | ctrl | 2020 | 0.25521 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0093
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | ctrl | 2030 | 0.25521 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0093
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | ctrl | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0093
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | lower | 2020 | 0.15951 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0093
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | lower | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0093
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | upper | 2020 | 0.36155 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0093
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | upper | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0093
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0104
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0104
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0104
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0104
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0104
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0104
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0104
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0104
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0115
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0115
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0115
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0115
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0115
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0115
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0115
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0115
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0204
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0204
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0204
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | ctrl | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0204
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0204
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | lower | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0204
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0204
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | upper | 2050 | 0 | life time extension of coal extraction plant - refurbish - coal - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0049 | tk_fin | manual_category_map | PAR_0204
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0021
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0021
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0021
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0021
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0021
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0086
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0086
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0086
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0086
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0086
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0170
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0170
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0170
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0170
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0170
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0178
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0178
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0178
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0178
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0049 | tk_reg | manual_category_map | PAR_0178
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2015 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0210
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0210
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2030 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0210
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | lower | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0210
ELH | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | upper | 2020 | 0 | life time extension of coal extraction plant - refurbish - coal - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0049 | tk_reg | manual_category_map | PAR_0210
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.02 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0016
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.02 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0016
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.02 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0016
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0016
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | upper | 2020 | -0.05 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0016
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2015 | 2 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | construction time [years] | ELH_0064 | tk_etd | manual_category_map | PAR_0026
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2020 | 2 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | construction time [years] | ELH_0064 | tk_etd | manual_category_map | PAR_0026
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2030 | 2 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | construction time [years] | ELH_0064 | tk_etd | manual_category_map | PAR_0026
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | lower | 2020 | 1.5 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | construction time [years] | ELH_0064 | tk_etd | manual_category_map | PAR_0026
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | upper | 2020 | 2.5 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | construction time [years] | ELH_0064 | tk_etd | manual_category_map | PAR_0026
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0029
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0029
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0029
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | lower | 2020 | -0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0029
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | upper | 2020 | 0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0064 | tk_etd | manual_category_map | PAR_0029
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0035
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0035
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0035
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0035
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | upper | 2020 | -0.02 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0035
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0037
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0037
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0037
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0037
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | upper | 2020 | -0.02 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0037
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0063
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0063
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0063
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | lower | 2020 | -0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0063
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0.01 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0064 | tk_etd | manual_category_map | PAR_0063
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 300 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0071
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 300 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0071
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 300 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0071
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 200 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0071
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 400 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0071
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0064 | tk_etd | manual_category_map | PAR_0166
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0064 | tk_etd | manual_category_map | PAR_0166
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0064 | tk_etd | manual_category_map | PAR_0166
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0064 | tk_etd | manual_category_map | PAR_0166
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0064 | tk_etd | manual_category_map | PAR_0166
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0185
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0185
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0185
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0185
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0064 | tk_etd | manual_category_map | PAR_0185
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2015 | 15 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0064 | tk_etd | manual_category_map | PAR_0198
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2020 | 15 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0064 | tk_etd | manual_category_map | PAR_0198
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2030 | 15 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0064 | tk_etd | manual_category_map | PAR_0198
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0018
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0018
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0018
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 3.1 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0018
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 3.1 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0018
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 1 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | n2o [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0089
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 1 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | n2o [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0089
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 1 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | n2o [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0089
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 0.8 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | n2o [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0089
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 0.8 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | n2o [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0089
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 20 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | nox [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0152
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 21 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | nox [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0152
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 18 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | nox [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0152
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 19 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | nox [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0152
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 53 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | nox [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0152
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0.3 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | particles [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0163
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0.3 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | particles [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0163
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0.3 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | environment | particles [g/gj_i] | ELH_0064 | tk_env | manual_category_map | PAR_0163
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | ctrl | 2015 | 3562.2986 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | fixed o&m [eur/mwe/year] | ELH_0064 | tk_fin | manual_category_map | PAR_0060
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | ctrl | 2020 | 3562.2986 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | fixed o&m [eur/mwe/year] | ELH_0064 | tk_fin | manual_category_map | PAR_0060
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | ctrl | 2030 | 3562.2986 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | fixed o&m [eur/mwe/year] | ELH_0064 | tk_fin | manual_category_map | PAR_0060
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | fixed o&m [eur/mwe/year] | ELH_0064 | tk_fin | manual_category_map | PAR_0060
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | lower | 2020 | 1435.5532 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | fixed o&m [eur/mwe/year] | ELH_0064 | tk_fin | manual_category_map | PAR_0060
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | lower | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | fixed o&m [eur/mwe/year] | ELH_0064 | tk_fin | manual_category_map | PAR_0060
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | upper | 2020 | 5689.044 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | fixed o&m [eur/mwe/year] | ELH_0064 | tk_fin | manual_category_map | PAR_0060
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | upper | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | fixed o&m [eur/mwe/year] | ELH_0064 | tk_fin | manual_category_map | PAR_0060
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | ctrl | 2015 | 0.53169 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0093
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | ctrl | 2020 | 0.53169 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0093
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | ctrl | 2030 | 0.53169 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0093
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0093
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | lower | 2020 | 0.37218 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0093
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | lower | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0093
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | upper | 2020 | 0.8507 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0093
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | upper | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0093
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0104
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0104
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0104
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0104
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0104
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0104
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0104
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0104
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0115
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0115
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0115
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0115
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0115
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0115
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0115
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0115
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | ctrl | 2015 | 0.95704 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0204
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | ctrl | 2020 | 0.95704 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0204
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | ctrl | 2030 | 0.95704 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0204
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0204
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | lower | 2020 | 0.42535 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0204
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | lower | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0204
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | upper | 2020 | 1.4887 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0204
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | upper | 2050 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0064 | tk_fin | manual_category_map | PAR_0204
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0021
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0021
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0021
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0021
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0021
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0086
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0086
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0086
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0086
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0086
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0170
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0170
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0170
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0170
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0170
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0178
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0178
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0178
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0178
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0064 | tk_reg | manual_category_map | PAR_0178
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0210
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0210
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0210
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0210
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0064 | tk_reg | manual_category_map | PAR_0210
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | ctrl | 2015 | 1350 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | fixed o&m (*total, additional to existing plant) [eur/mw_i/y] | ELH_0064 | tk_tsd | manual_category_map | PAR_0049
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | ctrl | 2020 | 1350 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | fixed o&m (*total, additional to existing plant) [eur/mw_i/y] | ELH_0064 | tk_tsd | manual_category_map | PAR_0049
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | ctrl | 2030 | 1350 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | fixed o&m (*total, additional to existing plant) [eur/mw_i/y] | ELH_0064 | tk_tsd | manual_category_map | PAR_0049
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | lower | 2020 | 550 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | fixed o&m (*total, additional to existing plant) [eur/mw_i/y] | ELH_0064 | tk_tsd | manual_category_map | PAR_0049
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | upper | 2020 | 2150 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | fixed o&m (*total, additional to existing plant) [eur/mw_i/y] | ELH_0064 | tk_tsd | manual_category_map | PAR_0049
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plant) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | ctrl | 2015 | 0.36 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | variable o&m (*total, additional to existing plant) [eur/mwh_i] | ELH_0064 | tk_tsd | manual_category_map | PAR_0205
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plant) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | ctrl | 2020 | 0.36 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | variable o&m (*total, additional to existing plant) [eur/mwh_i] | ELH_0064 | tk_tsd | manual_category_map | PAR_0205
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plant) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | ctrl | 2030 | 0.36 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | variable o&m (*total, additional to existing plant) [eur/mwh_i] | ELH_0064 | tk_tsd | manual_category_map | PAR_0205
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plant) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | lower | 2020 | 0.16 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | variable o&m (*total, additional to existing plant) [eur/mwh_i] | ELH_0064 | tk_tsd | manual_category_map | PAR_0205
ELH | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plant) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | upper | 2020 | 0.56 | rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | technology-specific data | variable o&m (*total, additional to existing plant) [eur/mwh_i] | ELH_0064 | tk_tsd | manual_category_map | PAR_0205
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | ctrl | 2015 | -0.07 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0016
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | ctrl | 2020 | -0.07 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0016
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | ctrl | 2030 | -0.07 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0016
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | lower | 2020 | -0.02 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0016
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | upper | 2020 | -0.1 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0016
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2015 | 2.5 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0065 | tk_etd | manual_category_map | PAR_0026
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2020 | 2.5 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0065 | tk_etd | manual_category_map | PAR_0026
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2030 | 2.5 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0065 | tk_etd | manual_category_map | PAR_0026
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | lower | 2020 | 2 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0065 | tk_etd | manual_category_map | PAR_0026
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | upper | 2020 | 3 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0065 | tk_etd | manual_category_map | PAR_0026
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0029
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0029
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0029
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | lower | 2020 | -0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0029
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | upper | 2020 | 0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0065 | tk_etd | manual_category_map | PAR_0029
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2015 | -0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0035
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2020 | -0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0035
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2030 | -0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0035
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0035
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | upper | 2020 | -0.02 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0035
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2015 | -0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0037
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2020 | -0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0037
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2030 | -0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0037
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0037
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | upper | 2020 | -0.02 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0037
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0063
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0063
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0063
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | lower | 2020 | -0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0063
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0.01 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0065 | tk_etd | manual_category_map | PAR_0063
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 300 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0071
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 300 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0071
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 300 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0071
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 200 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0071
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 400 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0071
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0065 | tk_etd | manual_category_map | PAR_0166
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0065 | tk_etd | manual_category_map | PAR_0166
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0065 | tk_etd | manual_category_map | PAR_0166
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0065 | tk_etd | manual_category_map | PAR_0166
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0065 | tk_etd | manual_category_map | PAR_0166
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2015 | 0.03 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0185
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2020 | 0.03 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0185
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2030 | 0.03 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0185
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | lower | 2020 | 0.02 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0185
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | upper | 2020 | 0.05 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0065 | tk_etd | manual_category_map | PAR_0185
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2015 | 15 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0065 | tk_etd | manual_category_map | PAR_0198
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2020 | 15 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0065 | tk_etd | manual_category_map | PAR_0198
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2030 | 15 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0065 | tk_etd | manual_category_map | PAR_0198
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 3 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0018
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 2 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0018
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 2 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0018
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0018
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 0.5 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0018
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 10 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0089
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 8 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0089
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 6 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0089
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 2 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0089
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 20 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0089
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 30 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0152
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 24 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0152
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 20 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0152
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 19 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0152
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 53 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0152
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0.3 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | particles [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0163
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0.3 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | particles [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0163
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0.3 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | particles [g/gj_i] | ELH_0065 | tk_env | manual_category_map | PAR_0163
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0.98 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0065 | tk_env | manual_category_map | PAR_0181
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0.98 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0065 | tk_env | manual_category_map | PAR_0181
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0.98 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0065 | tk_env | manual_category_map | PAR_0181
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | ctrl | 2015 | 78423.738 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0065 | tk_fin | manual_category_map | PAR_0042
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | ctrl | 2020 | 78423.738 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0065 | tk_fin | manual_category_map | PAR_0042
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | ctrl | 2030 | 78423.738 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0065 | tk_fin | manual_category_map | PAR_0042
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0065 | tk_fin | manual_category_map | PAR_0042
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | lower | 2020 | 65131.579 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0065 | tk_fin | manual_category_map | PAR_0042
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | lower | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0065 | tk_fin | manual_category_map | PAR_0042
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | upper | 2020 | 91715.8969 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0065 | tk_fin | manual_category_map | PAR_0042
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | upper | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0065 | tk_fin | manual_category_map | PAR_0042
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | ctrl | 2015 | 1.712 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0093
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | ctrl | 2020 | 1.712 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0093
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | ctrl | 2030 | 1.712 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0093
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0093
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | lower | 2020 | 1.4249 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0093
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | lower | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0093
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | upper | 2020 | 2.2863 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0093
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | upper | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0093
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0104
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0104
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0104
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0104
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0104
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0104
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0104
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0104
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0115
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0115
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0115
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0115
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0115
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0115
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0115
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0115
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | ctrl | 2015 | 2.9243 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0201
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | ctrl | 2020 | 2.9243 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0201
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | ctrl | 2030 | 2.9243 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0201
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0201
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | lower | 2020 | 1.8609 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0201
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | lower | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0201
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | upper | 2020 | 3.9876 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0201
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | upper | 2050 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0065 | tk_fin | manual_category_map | PAR_0201
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2015 | 1 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0021
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2020 | 1 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0021
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2030 | 1 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0021
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0021
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | upper | 2020 | 2 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0021
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0.0005 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0086
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0.0005 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0086
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0086
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0086
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0.001 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0086
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | ctrl | 2015 | -0.02 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0170
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0170
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0170
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0170
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | upper | 2020 | -0.05 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0170
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | ctrl | 2015 | -0.02 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0178
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0178
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0178
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0178
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | upper | 2020 | -0.05 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0065 | tk_reg | manual_category_map | PAR_0178
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2015 | 0.5 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0210
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2020 | 0.5 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0210
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0210
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0210
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | upper | 2020 | 2 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0065 | tk_reg | manual_category_map | PAR_0210
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | ctrl | 2015 | 29500 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0065 | tk_tsd | manual_category_map | PAR_0044
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | ctrl | 2020 | 29500 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0065 | tk_tsd | manual_category_map | PAR_0044
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | ctrl | 2030 | 29500 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0065 | tk_tsd | manual_category_map | PAR_0044
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | lower | 2020 | 24500 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0065 | tk_tsd | manual_category_map | PAR_0044
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | upper | 2020 | 34500 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0065 | tk_tsd | manual_category_map | PAR_0044
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | ctrl | 2015 | 1.1 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0065 | tk_tsd | manual_category_map | PAR_0203
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | ctrl | 2020 | 1.1 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0065 | tk_tsd | manual_category_map | PAR_0203
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | ctrl | 2030 | 1.1 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0065 | tk_tsd | manual_category_map | PAR_0203
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | lower | 2020 | 0.7 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0065 | tk_tsd | manual_category_map | PAR_0203
ELH | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | upper | 2020 | 1.5 | rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0065 | tk_tsd | manual_category_map | PAR_0203
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | ctrl | 2015 | -0.07 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0016
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | ctrl | 2020 | -0.07 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0016
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | ctrl | 2030 | -0.07 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0016
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | lower | 2020 | -0.02 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0016
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | upper | 2020 | -0.1 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cb coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0016
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2015 | 2 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0066 | tk_etd | manual_category_map | PAR_0026
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2020 | 2 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0066 | tk_etd | manual_category_map | PAR_0026
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2030 | 2 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0066 | tk_etd | manual_category_map | PAR_0026
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | lower | 2020 | 1.5 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0066 | tk_etd | manual_category_map | PAR_0026
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | upper | 2020 | 2.5 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | construction time [years] | ELH_0066 | tk_etd | manual_category_map | PAR_0026
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0029
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0029
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0029
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | lower | 2020 | -0.01 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0029
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | upper | 2020 | 0.01 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | cv coefficient (50°c/100°c, additional to existing plant) | ELH_0066 | tk_etd | manual_category_map | PAR_0029
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2015 | -0.03 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0035
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2020 | -0.03 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0035
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2030 | -0.03 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0035
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | lower | 2020 | -0.02 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0035
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | upper | 2020 | -0.04 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, annual average, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0035
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2015 | -0.03 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0037
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2020 | -0.03 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0037
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2030 | -0.03 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0037
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | lower | 2020 | -0.02 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0037
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | upper | 2020 | -0.04 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | electrical efficiency (net, name plate, additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0037
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0063
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0063
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0063
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | lower | 2020 | -0.01 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0063
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0.01 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | forced outage (additional to existing plant) [] | ELH_0066 | tk_etd | manual_category_map | PAR_0063
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 300 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0071
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 300 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0071
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 300 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0071
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 200 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0071
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 400 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0071
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0066 | tk_etd | manual_category_map | PAR_0166
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0066 | tk_etd | manual_category_map | PAR_0166
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0066 | tk_etd | manual_category_map | PAR_0166
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0066 | tk_etd | manual_category_map | PAR_0166
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | planned outage (additional to existing plant) [weeks per year] | ELH_0066 | tk_etd | manual_category_map | PAR_0166
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2015 | 0.04 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0185
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2020 | 0.04 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0185
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2030 | 0.04 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0185
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | lower | 2020 | 0.03 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0185
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | upper | 2020 | 0.06 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | space requirement (additional to existing plant) [1000 m2/mw_e] | ELH_0066 | tk_etd | manual_category_map | PAR_0185
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2015 | 15 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0066 | tk_etd | manual_category_map | PAR_0198
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2020 | 15 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0066 | tk_etd | manual_category_map | PAR_0198
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2030 | 15 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0066 | tk_etd | manual_category_map | PAR_0198
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 3 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0018
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 2 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0018
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 2 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0018
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 3.1 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0018
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 3.1 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | ch4 [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0018
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 10 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0089
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 8 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0089
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 6 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0089
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 0.8 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0089
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 0.8 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | n2o [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0089
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 30 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0152
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 24 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0152
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 20 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0152
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 19 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0152
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 53 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | nox [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0152
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 0.3 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | particles [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0163
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 0.3 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | particles [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0163
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 0.3 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | particles [g/gj_i] | ELH_0066 | tk_env | manual_category_map | PAR_0163
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G |  | ctrl | 2015 | 0.98 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0066 | tk_env | manual_category_map | PAR_0181
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G |  | ctrl | 2020 | 0.98 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0066 | tk_env | manual_category_map | PAR_0181
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G |  | ctrl | 2030 | 0.98 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0066 | tk_env | manual_category_map | PAR_0181
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | ctrl | 2015 | 15073.3083 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0066 | tk_fin | manual_category_map | PAR_0048
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | ctrl | 2020 | 15073.3083 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0066 | tk_fin | manual_category_map | PAR_0048
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | ctrl | 2030 | 15073.3083 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0066 | tk_fin | manual_category_map | PAR_0048
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0066 | tk_fin | manual_category_map | PAR_0048
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | lower | 2020 | 13398.4962 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0066 | tk_fin | manual_category_map | PAR_0048
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | lower | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0066 | tk_fin | manual_category_map | PAR_0048
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | upper | 2020 | 16748.1203 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0066 | tk_fin | manual_category_map | PAR_0048
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | upper | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | fixed o&m (*total, additional to existing plant) [eur/mw_e/y] | ELH_0066 | tk_fin | manual_category_map | PAR_0048
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | ctrl | 2015 | 1.712 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0093
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | ctrl | 2020 | 1.712 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0093
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | ctrl | 2030 | 1.712 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0093
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0093
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | lower | 2020 | 1.4249 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0093
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | lower | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0093
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | upper | 2020 | 2.2863 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0093
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | upper | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0093
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0104
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0104
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0104
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0104
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0104
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0104
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0104
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0104
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0115
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0115
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0115
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0115
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0115
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0115
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0115
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0115
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | ctrl | 2015 | 1.5951 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0204
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | ctrl | 2020 | 1.5951 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0204
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | ctrl | 2030 | 1.5951 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0204
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0204
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | lower | 2020 | 1.0634 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0204
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | lower | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0204
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | upper | 2020 | 2.1267 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0204
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | upper | 2050 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | financial data | variable o&m (*total, additional to existing plant) [eur/mwh_e] | ELH_0066 | tk_fin | manual_category_map | PAR_0204
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0021
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0021
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0021
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0021
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | cold start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0021
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0086
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0086
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0086
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0086
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | minimum load (of full load, additional to existing plant) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0086
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0170
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0170
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0170
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0170
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | primary regulation (of full load, additional to existing plant, per 30 seconds) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0170
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0178
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0178
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0178
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0178
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | secondary regulation (of full load, additional to existing plant, per minute) [] | ELH_0066 | tk_reg | manual_category_map | PAR_0178
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0210
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0210
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0210
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | lower | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0210
ELH | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | upper | 2020 | 0 | rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | regulation ability | warm start-up time (additional to existing plant) [hours] | ELH_0066 | tk_reg | manual_category_map | PAR_0210
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | B | 13 | ctrl | 2015 | 0.35 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0067 | tk_etd | manual_category_map | PAR_0015
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | 13 | ctrl | 2015 | 0.0027 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0067 | tk_etd | manual_category_map | PAR_0034
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Forced outage [] |  |  | C | 13 | ctrl | 2015 | 0.03 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | energy/technical data | forced outage [] | ELH_0067 | tk_etd | manual_category_map | PAR_0065
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, E] | 13 | ctrl | 2015 | 70 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0067 | tk_etd | manual_category_map | PAR_0071
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, E] | 13 | lower | 2020 | 50 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0067 | tk_etd | manual_category_map | PAR_0071
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, E] | 13 | upper | 2020 | 90 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0067 | tk_etd | manual_category_map | PAR_0071
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 13 | ctrl | 2015 | 1.56 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0067 | tk_etd | manual_category_map | PAR_0168
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 15 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0067 | tk_etd | manual_category_map | PAR_0198
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | C | 13 | ctrl | 2015 | 3 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | environment | ch4 [g/gj_i] | ELH_0067 | tk_env | manual_category_map | PAR_0018
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | C | 13 | ctrl | 2015 | 10 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | environment | n2o [g/gj_i] | ELH_0067 | tk_env | manual_category_map | PAR_0089
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | C | 13 | ctrl | 2015 | 30 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | environment | nox [g/gj_i] | ELH_0067 | tk_env | manual_category_map | PAR_0152
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | C | 13 | ctrl | 2015 | 0.3 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | environment | particles [g/gj_i] | ELH_0067 | tk_env | manual_category_map | PAR_0163
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | ctrl | 2015 | 116183.3163 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0067 | tk_fin | manual_category_map | PAR_0042
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0067 | tk_fin | manual_category_map | PAR_0042
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0067 | tk_fin | manual_category_map | PAR_0042
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0067 | tk_fin | manual_category_map | PAR_0042
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0067 | tk_fin | manual_category_map | PAR_0042
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0067 | tk_fin | manual_category_map | PAR_0042
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0067 | tk_fin | manual_category_map | PAR_0042
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0067 | tk_fin | manual_category_map | PAR_0042
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0093
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0093
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0093
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0093
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0093
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0093
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0093
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0093
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0104
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0104
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0104
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0104
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0104
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0104
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0104
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0104
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0115
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0115
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0115
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0115
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0115
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0115
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0115
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0115
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | ctrl | 2015 | 4.3279 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0201
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | ctrl | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0201
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | ctrl | 2030 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0201
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | ctrl | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0201
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | lower | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0201
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | lower | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0201
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | upper | 2020 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0201
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | upper | 2050 | 0 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0067 | tk_fin | manual_category_map | PAR_0201
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  | C | 13 | ctrl | 2015 | 12 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0067 | tk_reg | manual_category_map | PAR_0022
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | C | 13 | ctrl | 2015 | 0.45 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0067 | tk_reg | manual_category_map | PAR_0085
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | C | 13 | ctrl | 2015 | 0.02 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0067 | tk_reg | manual_category_map | PAR_0171
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 13 | ctrl | 2015 | 0.03 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0067 | tk_reg | manual_category_map | PAR_0179
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | C | 13 | ctrl | 2015 | 2 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0067 | tk_reg | manual_category_map | PAR_0211
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | D |  | ctrl | 2015 | 29500 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0067 | tk_tsd | manual_category_map | PAR_0044
ELH | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | D |  | ctrl | 2015 | 1.1 | rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0067 | tk_tsd | manual_category_map | PAR_0203
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2015 | 0.95 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0034 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2020 | 0.96 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0034 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2030 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0034 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0034 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | lower | 2020 | 0.8 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0034 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | lower | 2050 | 0.8 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0034 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | upper | 2020 | 1.2 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0034 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | upper | 2050 | 1.2 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0034 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2015 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | construction time [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2020 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | construction time [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2030 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | construction time [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2050 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | construction time [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | lower | 2020 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | construction time [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | lower | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | construction time [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | upper | 2020 | 2 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | construction time [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | upper | 2050 | 2 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | construction time [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2015 | 0.39 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2020 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2030 | 0.41 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2050 | 0.43 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | lower | 2020 | 0.36 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | lower | 2050 | 0.38 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | upper | 2020 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | upper | 2050 | 0.42 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | ctrl | 2015 | 0.41 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | ctrl | 2020 | 0.42 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | ctrl | 2030 | 0.43 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | ctrl | 2050 | 0.45 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | lower | 2020 | 0.38 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | lower | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | upper | 2020 | 0.42 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | upper | 2050 | 0.44 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0034 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2015 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | forced outage [] | ELH_0034 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2020 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | forced outage [] | ELH_0034 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2030 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | forced outage [] | ELH_0034 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2050 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | forced outage [] | ELH_0034 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | lower | 2020 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | forced outage [] | ELH_0034 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | lower | 2050 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | forced outage [] | ELH_0034 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | upper | 2020 | 0.03 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | forced outage [] | ELH_0034 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | upper | 2050 | 0.03 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | forced outage [] | ELH_0034 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2020 | 40 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2050 | 40 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2020 | 125 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2050 | 125 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2015 | 3 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0034 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2020 | 3 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0034 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2030 | 2.5 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0034 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2050 | 2.5 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0034 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2020 | 2 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0034 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2050 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0034 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2020 | 3.5 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0034 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2050 | 3 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0034 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2015 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2020 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2030 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2050 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | lower | 2020 | 0.01 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | lower | 2050 | 0.01 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | upper | 2020 | 0.03 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | upper | 2050 | 0.03 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0034 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2015 | 25 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2020 | 25 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2030 | 25 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2050 | 25 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | lower | 2020 | 25 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | lower | 2050 | 25 | gas turbine, simple cycle - back pressure - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0034 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2015 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | environment | ch4 [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2020 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | environment | ch4 [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2030 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | environment | ch4 [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2050 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - large | environment | ch4 [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | lower | 2020 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | environment | ch4 [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | lower | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | environment | ch4 [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | upper | 2020 | 8 | gas turbine, simple cycle - back pressure - natural gas - large | environment | ch4 [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | upper | 2050 | 8 | gas turbine, simple cycle - back pressure - natural gas - large | environment | ch4 [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2015 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | environment | n2o [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2020 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | environment | n2o [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2030 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | environment | n2o [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | environment | n2o [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | lower | 2020 | 0.7 | gas turbine, simple cycle - back pressure - natural gas - large | environment | n2o [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | lower | 2050 | 0.7 | gas turbine, simple cycle - back pressure - natural gas - large | environment | n2o [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | upper | 2020 | 1.2 | gas turbine, simple cycle - back pressure - natural gas - large | environment | n2o [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | upper | 2050 | 1.2 | gas turbine, simple cycle - back pressure - natural gas - large | environment | n2o [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2015 | 20 | gas turbine, simple cycle - back pressure - natural gas - large | environment | nox [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2020 | 15 | gas turbine, simple cycle - back pressure - natural gas - large | environment | nox [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2030 | 10 | gas turbine, simple cycle - back pressure - natural gas - large | environment | nox [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2050 | 10 | gas turbine, simple cycle - back pressure - natural gas - large | environment | nox [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | lower | 2020 | 10 | gas turbine, simple cycle - back pressure - natural gas - large | environment | nox [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | lower | 2050 | 7.5 | gas turbine, simple cycle - back pressure - natural gas - large | environment | nox [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | upper | 2020 | 30 | gas turbine, simple cycle - back pressure - natural gas - large | environment | nox [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | upper | 2050 | 20 | gas turbine, simple cycle - back pressure - natural gas - large | environment | nox [g/gj_i] | ELH_0034 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0034 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0034 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0034 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0034 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0034 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0034 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0034 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0034 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2015 | 21267.4544 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0034 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2020 | 20735.768 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0034 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2030 | 19778.7326 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0034 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2050 | 19140.7089 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0034 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0034 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0034 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0034 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0034 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2015 | 0.63802 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2020 | 0.62739 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2030 | 0.59549 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2050 | 0.55295 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | lower | 2020 | 0.42535 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | lower | 2050 | 0.37218 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | upper | 2020 | 0.95704 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | upper | 2050 | 0.90387 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2015 | 4.7852 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2020 | 4.6788 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2030 | 4.4662 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2050 | 4.2535 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | lower | 2020 | 4.2535 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | lower | 2050 | 3.1901 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | upper | 2020 | 6.3802 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | upper | 2050 | 5.3169 | gas turbine, simple cycle - back pressure - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0034 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2020 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2020 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2015 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2020 | 0.23 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2030 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | lower | 2020 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | lower | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | upper | 2020 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | upper | 2050 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2015 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2020 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2030 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | lower | 2020 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | lower | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | upper | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | upper | 2050 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0034 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.23 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2020 | 0.1 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2050 | 0.1 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0034 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2015 | 0.71 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0036 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2020 | 0.73 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0036 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2030 | 0.8 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0036 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2050 | 0.8 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0036 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | lower | 2020 | 0.61 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0036 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | lower | 2050 | 0.7 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0036 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | upper | 2020 | 0.8 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0036 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | upper | 2050 | 0.9 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0036 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2015 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2020 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2030 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2050 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | lower | 2020 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | lower | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | upper | 2020 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | upper | 2050 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2015 | 0.34 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2020 | 0.35 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2030 | 0.37 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2050 | 0.38 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | lower | 2020 | 0.3 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | lower | 2050 | 0.32 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | upper | 2020 | 0.38 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | upper | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | ctrl | 2015 | 0.36 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | ctrl | 2020 | 0.37 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | ctrl | 2030 | 0.39 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | ctrl | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | lower | 2020 | 0.32 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | lower | 2050 | 0.34 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | upper | 2020 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | upper | 2050 | 0.42 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0036 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2015 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0036 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2020 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0036 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2030 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0036 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2050 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0036 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | lower | 2020 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0036 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | lower | 2050 | 0.02 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0036 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | upper | 2020 | 0.03 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0036 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | upper | 2050 | 0.03 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0036 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2020 | 5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2050 | 5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2020 | 40 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2050 | 40 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2015 | 3 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0036 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2020 | 2.8 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0036 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2030 | 2.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0036 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2050 | 2.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0036 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2020 | 2 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0036 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2050 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0036 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2020 | 3.5 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0036 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2050 | 3 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0036 | tk_etd | manual_category_map | PAR_0168
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2015 | 0.04 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2020 | 0.04 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2030 | 0.04 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2050 | 0.04 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | lower | 2020 | 0.03 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | lower | 2050 | 0.03 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | upper | 2020 | 0.07 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | upper | 2050 | 0.07 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0036 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2015 | 25 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2020 | 25 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2030 | 25 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2050 | 25 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | lower | 2020 | 25 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | lower | 2050 | 25 | gas turbine, simple cycle - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0036 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2015 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2020 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2030 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2050 | 1.5 | gas turbine, simple cycle - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2020 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2020 | 8 | gas turbine, simple cycle - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2050 | 8 | gas turbine, simple cycle - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2015 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2020 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2030 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2020 | 0.7 | gas turbine, simple cycle - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2050 | 0.7 | gas turbine, simple cycle - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2020 | 1.2 | gas turbine, simple cycle - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2050 | 1.2 | gas turbine, simple cycle - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0089
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2015 | 20 | gas turbine, simple cycle - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2020 | 15 | gas turbine, simple cycle - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2030 | 10 | gas turbine, simple cycle - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2050 | 10 | gas turbine, simple cycle - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | lower | 2020 | 10 | gas turbine, simple cycle - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | lower | 2050 | 8 | gas turbine, simple cycle - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | upper | 2020 | 30 | gas turbine, simple cycle - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | upper | 2050 | 20 | gas turbine, simple cycle - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0036 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0036 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0036 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0036 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0036 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0036 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0036 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0036 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0036 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2015 | 21267.4544 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0036 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2020 | 20735.768 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0036 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2030 | 19778.7326 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0036 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2050 | 19140.7089 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0036 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0036 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0036 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0036 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0036 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2015 | 0.79753 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2020 | 0.77626 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2030 | 0.74436 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2050 | 0.72309 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | lower | 2020 | 0.63802 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | lower | 2050 | 0.58485 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | upper | 2020 | 1.0634 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | upper | 2050 | 1.0102 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2015 | 5.8485 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2020 | 5.7422 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2030 | 5.4232 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2050 | 4.8915 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | lower | 2020 | 5.3169 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | lower | 2050 | 4.2535 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | upper | 2020 | 7.4436 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | upper | 2050 | 6.3802 | gas turbine, simple cycle - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0036 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2020 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2020 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2050 | 1 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2015 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2020 | 0.23 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2030 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | lower | 2020 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | lower | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | upper | 2020 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | upper | 2050 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2015 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2020 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2030 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | lower | 2020 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | lower | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | upper | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | upper | 2050 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0036 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.23 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2020 | 0.1 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2050 | 0.1 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0036 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | ctrl | 2015 | 0.6 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | cb coefficient (50°c/100°c) | ELH_0035 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | ctrl | 2020 | 0.6 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | cb coefficient (50°c/100°c) | ELH_0035 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | ctrl | 2030 | 0.6 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | cb coefficient (50°c/100°c) | ELH_0035 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | ctrl | 2050 | 0.6 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | cb coefficient (50°c/100°c) | ELH_0035 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | lower | 2020 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | cb coefficient (50°c/100°c) | ELH_0035 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | lower | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | cb coefficient (50°c/100°c) | ELH_0035 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | upper | 2020 | 0.85 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | cb coefficient (50°c/100°c) | ELH_0035 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | upper | 2050 | 0.85 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | cb coefficient (50°c/100°c) | ELH_0035 | tk_etd | manual_category_map | PAR_0015
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | ctrl | 2015 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | construction time [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | ctrl | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | construction time [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | ctrl | 2030 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | construction time [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | ctrl | 2050 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | construction time [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | lower | 2020 | 0.3 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | construction time [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | lower | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | construction time [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | upper | 2020 | 0.8 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | construction time [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | upper | 2050 | 0.7 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | construction time [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0026
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | ctrl | 2015 | 0.28 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | ctrl | 2020 | 0.28 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | ctrl | 2030 | 0.28 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | ctrl | 2050 | 0.28 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | lower | 2020 | 0.21 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | lower | 2050 | 0.23 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | upper | 2020 | 0.29 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | upper | 2050 | 0.33 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0034
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | ctrl | 2015 | 0.3 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | ctrl | 2020 | 0.3 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | ctrl | 2030 | 0.3 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | ctrl | 2050 | 0.3 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | lower | 2020 | 0.23 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | lower | 2050 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | upper | 2020 | 0.32 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | upper | 2050 | 0.35 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0035 | tk_etd | manual_category_map | PAR_0036
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.05 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | forced outage [] | ELH_0035 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.05 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | forced outage [] | ELH_0035 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.05 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | forced outage [] | ELH_0035 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.05 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | forced outage [] | ELH_0035 | tk_etd | manual_category_map | PAR_0065
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 0.01 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | generating capacity for one unit [mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 0.01 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | generating capacity for one unit [mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | generating capacity for one unit [mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 0.2 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | generating capacity for one unit [mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0071
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | ctrl | 2015 | 0.06 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | ctrl | 2020 | 0.06 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | ctrl | 2030 | 0.06 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | ctrl | 2050 | 0.06 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | lower | 2020 | 0.05 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | lower | 2050 | 0.05 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | upper | 2020 | 0.15 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | upper | 2050 | 0.15 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0035 | tk_etd | manual_category_map | PAR_0188
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | ctrl | 2015 | 15 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | technical lifetime [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | ctrl | 2020 | 15 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | technical lifetime [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | ctrl | 2030 | 15 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | technical lifetime [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | ctrl | 2050 | 15 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | technical lifetime [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | lower | 2020 | 10 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | technical lifetime [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | lower | 2050 | 10 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | technical lifetime [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | upper | 2020 | 20 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | technical lifetime [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | upper | 2050 | 20 | gas turbine, simple cycle - back pressure - natural gas - micro | energy/technical data | technical lifetime [years] | ELH_0035 | tk_etd | manual_category_map | PAR_0198
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 13 | ctrl | 2015 | 6 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | ch4 [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 13 | ctrl | 2020 | 6 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | ch4 [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 13 | ctrl | 2030 | 6 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | ch4 [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 13 | ctrl | 2050 | 6 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | ch4 [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0018
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | ctrl | 2015 | 10 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | nox [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | ctrl | 2020 | 10 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | nox [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | ctrl | 2030 | 10 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | nox [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | ctrl | 2050 | 10 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | nox [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | lower | 2020 | 6 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | nox [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | lower | 2050 | 6 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | nox [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | upper | 2020 | 15 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | nox [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | upper | 2050 | 15 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | nox [g/gj_i] | ELH_0035 | tk_env | manual_category_map | PAR_0152
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | so2 (degree of desulphuring) [] | ELH_0035 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | so2 (degree of desulphuring) [] | ELH_0035 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | so2 (degree of desulphuring) [] | ELH_0035 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | so2 (degree of desulphuring) [] | ELH_0035 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | so2 (degree of desulphuring) [] | ELH_0035 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | so2 (degree of desulphuring) [] | ELH_0035 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | so2 (degree of desulphuring) [] | ELH_0035 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | environment | so2 (degree of desulphuring) [] | ELH_0035 | tk_env | manual_category_map | PAR_0181
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0035 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0035 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0035 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0035 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0035 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0035 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0035 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0035 | tk_fin | manual_category_map | PAR_0042
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2015 | 1.276 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (*total) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2020 | 1.276 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (*total) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2030 | 1.1697 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (*total) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2050 | 1.0634 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (*total) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (*total) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (*total) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (*total) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (*total) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0093
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2015 | 0.90387 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2020 | 0.90387 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2030 | 0.8507 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2050 | 0.74436 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0104
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2015 | 0.37218 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (installation) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2020 | 0.37218 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (installation) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2030 | 0.31901 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (installation) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2050 | 0.31901 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (installation) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (installation) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (installation) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (installation) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | nominal investment (installation) [meur/mw_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0115
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | ctrl | 2015 | 15.9506 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | ctrl | 2020 | 15.9506 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | ctrl | 2030 | 14.8872 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | ctrl | 2050 | 13.8238 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | lower | 2020 | 10.6337 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | lower | 2050 | 8.507 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | upper | 2020 | 15.9506 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | upper | 2050 | 15.9506 | gas turbine, simple cycle - back pressure - natural gas - micro | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0035 | tk_fin | manual_category_map | PAR_0201
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | cold start-up time [hours] | ELH_0035 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | cold start-up time [hours] | ELH_0035 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | cold start-up time [hours] | ELH_0035 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | cold start-up time [hours] | ELH_0035 | tk_reg | manual_category_map | PAR_0022
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | ctrl | 2015 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | minimum load (of full load) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | ctrl | 2020 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | minimum load (of full load) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | ctrl | 2030 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | minimum load (of full load) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | ctrl | 2050 | 0.4 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | minimum load (of full load) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | lower | 2020 | 0.3 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | minimum load (of full load) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | lower | 2050 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | minimum load (of full load) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | upper | 2020 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | minimum load (of full load) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | upper | 2050 | 0.5 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | minimum load (of full load) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0085
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0171
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2015 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2030 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2020 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2050 | 0 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0035 | tk_reg | manual_category_map | PAR_0179
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | warm start-up time [hours] | ELH_0035 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | warm start-up time [hours] | ELH_0035 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | warm start-up time [hours] | ELH_0035 | tk_reg | manual_category_map | PAR_0211
ELH | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.25 | gas turbine, simple cycle - back pressure - natural gas - micro | regulation ability | warm start-up time [hours] | ELH_0035 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 1.7 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 1.8 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 2.2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 2.2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 2.4 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2015 | 2.5 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | construction time [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 2.5 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | construction time [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 2.5 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | construction time [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 2.5 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | construction time [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2020 | 2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | construction time [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | construction time [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2020 | 3 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | construction time [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 3 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | construction time [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | J |  | ctrl | 2015 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0028
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | J |  | ctrl | 2020 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0028
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | J |  | ctrl | 2030 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0028
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | J |  | ctrl | 2050 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0031 | tk_etd | manual_category_map | PAR_0028
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2015 | 0.55 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2020 | 0.56 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2030 | 0.58 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2050 | 0.6 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | lower | 2020 | 0.52 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | lower | 2050 | 0.55 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | upper | 2020 | 0.58 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | upper | 2050 | 0.62 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2015 | 0.58 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2020 | 0.59 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2030 | 0.61 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2050 | 0.63 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | lower | 2020 | 0.55 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | lower | 2050 | 0.58 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | upper | 2020 | 0.61 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | upper | 2050 | 0.65 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0031 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2015 | 0.03 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | forced outage [] | ELH_0031 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.03 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | forced outage [] | ELH_0031 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.03 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | forced outage [] | ELH_0031 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.03 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | forced outage [] | ELH_0031 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2020 | 0.02 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | forced outage [] | ELH_0031 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.02 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | forced outage [] | ELH_0031 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2020 | 0.04 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | forced outage [] | ELH_0031 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.04 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | forced outage [] | ELH_0031 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2020 | 100 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0071
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2050 | 100 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0071
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2020 | 500 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0071
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2050 | 500 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0071
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2015 | 2.5 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0031 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2.3 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0031 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0031 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0031 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2020 | 2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0031 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 2 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0031 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2020 | 4 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0031 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | planned outage [weeks per year] | ELH_0031 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2015 | 0.02 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2020 | 0.02 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2030 | 0.02 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2050 | 0.02 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | lower | 2020 | 0.01 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | lower | 2050 | 0.01 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | upper | 2020 | 0.03 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | upper | 2050 | 0.03 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0031 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2015 | 25 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2020 | 25 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2030 | 25 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2050 | 25 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | lower | 2020 | 25 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | lower | 2050 | 25 | gas turbine, combined cycle - extraction - natural gas - large | energy/technical data | technical lifetime [years] | ELH_0031 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2015 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | environment | ch4 [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2020 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | environment | ch4 [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2030 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | environment | ch4 [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2050 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | environment | ch4 [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2020 | 1 | gas turbine, combined cycle - extraction - natural gas - large | environment | ch4 [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2050 | 1 | gas turbine, combined cycle - extraction - natural gas - large | environment | ch4 [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2020 | 8 | gas turbine, combined cycle - extraction - natural gas - large | environment | ch4 [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2050 | 8 | gas turbine, combined cycle - extraction - natural gas - large | environment | ch4 [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2015 | 1 | gas turbine, combined cycle - extraction - natural gas - large | environment | n2o [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2020 | 1 | gas turbine, combined cycle - extraction - natural gas - large | environment | n2o [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2030 | 1 | gas turbine, combined cycle - extraction - natural gas - large | environment | n2o [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2050 | 1 | gas turbine, combined cycle - extraction - natural gas - large | environment | n2o [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2020 | 0.7 | gas turbine, combined cycle - extraction - natural gas - large | environment | n2o [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2050 | 0.7 | gas turbine, combined cycle - extraction - natural gas - large | environment | n2o [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2020 | 1.2 | gas turbine, combined cycle - extraction - natural gas - large | environment | n2o [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2050 | 1.2 | gas turbine, combined cycle - extraction - natural gas - large | environment | n2o [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2015 | 20 | gas turbine, combined cycle - extraction - natural gas - large | environment | nox [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2020 | 15 | gas turbine, combined cycle - extraction - natural gas - large | environment | nox [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2030 | 10 | gas turbine, combined cycle - extraction - natural gas - large | environment | nox [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2050 | 8 | gas turbine, combined cycle - extraction - natural gas - large | environment | nox [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | lower | 2020 | 10 | gas turbine, combined cycle - extraction - natural gas - large | environment | nox [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | lower | 2050 | 5 | gas turbine, combined cycle - extraction - natural gas - large | environment | nox [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | upper | 2020 | 30 | gas turbine, combined cycle - extraction - natural gas - large | environment | nox [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | upper | 2050 | 15 | gas turbine, combined cycle - extraction - natural gas - large | environment | nox [g/gj_i] | ELH_0031 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0 | gas turbine, combined cycle - extraction - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0031 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0 | gas turbine, combined cycle - extraction - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0031 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0 | gas turbine, combined cycle - extraction - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0031 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 0 | gas turbine, combined cycle - extraction - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0031 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2020 | 0 | gas turbine, combined cycle - extraction - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0031 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2050 | 0 | gas turbine, combined cycle - extraction - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0031 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2020 | 0 | gas turbine, combined cycle - extraction - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0031 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2050 | 0 | gas turbine, combined cycle - extraction - natural gas - large | environment | so2 (degree of desulphuring) [] | ELH_0031 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2015 | 31901.1815 | gas turbine, combined cycle - extraction - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0031 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2020 | 31156.8206 | gas turbine, combined cycle - extraction - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0031 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2030 | 29561.7616 | gas turbine, combined cycle - extraction - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0031 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2050 | 27647.6907 | gas turbine, combined cycle - extraction - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0031 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | lower | 2020 | 26584.318 | gas turbine, combined cycle - extraction - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0031 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | lower | 2050 | 21267.4544 | gas turbine, combined cycle - extraction - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0031 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | upper | 2020 | 37218.0451 | gas turbine, combined cycle - extraction - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0031 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | upper | 2050 | 31901.1815 | gas turbine, combined cycle - extraction - natural gas - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0031 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | ctrl | 2015 | 0.95704 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | ctrl | 2020 | 0.93577 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | ctrl | 2030 | 0.8826 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | ctrl | 2050 | 0.8507 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | lower | 2020 | 0.8507 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | lower | 2050 | 0.74436 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | upper | 2020 | 1.276 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | upper | 2050 | 1.1697 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2015 | 0.74436 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2020 | 0.72309 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2030 | 0.68056 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2050 | 0.64866 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2020 | 0.69119 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2050 | 0.63802 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2020 | 1.0846 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2050 | 1.0102 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2015 | 0.21267 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2020 | 0.21267 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2030 | 0.20204 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2050 | 0.20204 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2020 | 0.15951 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2050 | 0.10634 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2020 | 0.19141 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2050 | 0.15951 | gas turbine, combined cycle - extraction - natural gas - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2015 | 4.7852 | gas turbine, combined cycle - extraction - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2020 | 4.6788 | gas turbine, combined cycle - extraction - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2030 | 4.4662 | gas turbine, combined cycle - extraction - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2050 | 4.2535 | gas turbine, combined cycle - extraction - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | lower | 2020 | 3.1901 | gas turbine, combined cycle - extraction - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | lower | 2050 | 3.1901 | gas turbine, combined cycle - extraction - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | upper | 2020 | 7.4436 | gas turbine, combined cycle - extraction - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | upper | 2050 | 7.4436 | gas turbine, combined cycle - extraction - natural gas - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0031 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2015 | 2.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2020 | 2.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2030 | 2.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2050 | 2 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | lower | 2020 | 2 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | lower | 2050 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | upper | 2020 | 5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | upper | 2050 | 5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | cold start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2015 | 0.4 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2020 | 0.4 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2030 | 0.4 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2050 | 0.4 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | lower | 2020 | 0.3 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | lower | 2050 | 0.3 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | upper | 2020 | 0.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | upper | 2050 | 0.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | minimum load (of full load) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | ctrl | 2015 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | ctrl | 2020 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | ctrl | 2030 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | ctrl | 2050 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | lower | 2020 | 0.05 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | lower | 2050 | 0.05 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | upper | 2020 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | upper | 2050 | 0.15 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0031 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2015 | 1 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2020 | 1 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2030 | 1 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2050 | 1 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | lower | 2020 | 0.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | lower | 2050 | 0.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | upper | 2020 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | upper | 2050 | 1.5 | gas turbine, combined cycle - extraction - natural gas - large | regulation ability | warm start-up time [hours] | ELH_0031 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 1.2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0030 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 1.3 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0030 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 1.4 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0030 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 1.55 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0030 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.9 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0030 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 1.1 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0030 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 1.6 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0030 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 1.7 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | cb coefficient (50°c/100°c) | ELH_0030 | tk_etd | manual_category_map | PAR_0015
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2015 | 2.5 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | construction time [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | construction time [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | construction time [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | construction time [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2020 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | construction time [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | construction time [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2020 | 3 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | construction time [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 3 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | construction time [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0026
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2015 | 0.47 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2020 | 0.48 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2030 | 0.5 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2050 | 0.52 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | lower | 2020 | 0.39 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | lower | 2050 | 0.42 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | upper | 2020 | 0.52 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | upper | 2050 | 0.55 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0034
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2015 | 0.5 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2020 | 0.51 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2030 | 0.53 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2050 | 0.55 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | lower | 2020 | 0.42 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | lower | 2050 | 0.45 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | upper | 2020 | 0.55 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | upper | 2050 | 0.58 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0030 | tk_etd | manual_category_map | PAR_0036
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2015 | 0.03 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | forced outage [] | ELH_0030 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.03 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | forced outage [] | ELH_0030 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.03 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | forced outage [] | ELH_0030 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.03 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | forced outage [] | ELH_0030 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2020 | 0.02 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | forced outage [] | ELH_0030 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.02 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | forced outage [] | ELH_0030 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2020 | 0.04 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | forced outage [] | ELH_0030 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.04 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | forced outage [] | ELH_0030 | tk_etd | manual_category_map | PAR_0065
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2020 | 10 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0071
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2050 | 10 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0071
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2020 | 100 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0071
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2050 | 100 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0071
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2015 | 2.5 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | planned outage [weeks per year] | ELH_0030 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2.3 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | planned outage [weeks per year] | ELH_0030 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | planned outage [weeks per year] | ELH_0030 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | planned outage [weeks per year] | ELH_0030 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2020 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | planned outage [weeks per year] | ELH_0030 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1.5 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | planned outage [weeks per year] | ELH_0030 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2020 | 4 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | planned outage [weeks per year] | ELH_0030 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | planned outage [weeks per year] | ELH_0030 | tk_etd | manual_category_map | PAR_0168
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2015 | 0.03 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2020 | 0.03 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2030 | 0.03 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2050 | 0.03 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | lower | 2020 | 0.02 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | lower | 2050 | 0.02 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | upper | 2020 | 0.04 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | upper | 2050 | 0.04 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0030 | tk_etd | manual_category_map | PAR_0188
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2015 | 25 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | technical lifetime [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2020 | 25 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | technical lifetime [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2030 | 25 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | technical lifetime [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2050 | 25 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | technical lifetime [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | lower | 2020 | 25 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | technical lifetime [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | lower | 2050 | 25 | gas turbine, combined cycle - back pressure - natural gas - medium | energy/technical data | technical lifetime [years] | ELH_0030 | tk_etd | manual_category_map | PAR_0198
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2015 | 1.5 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | ch4 [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2020 | 1.5 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | ch4 [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2030 | 1.5 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | ch4 [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2050 | 1.5 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | ch4 [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2020 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | ch4 [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2050 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | ch4 [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2020 | 8 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | ch4 [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2050 | 8 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | ch4 [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0018
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2015 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | n2o [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2020 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | n2o [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2030 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | n2o [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2050 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | n2o [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2020 | 0.7 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | n2o [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2050 | 0.7 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | n2o [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2020 | 1.2 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | n2o [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2050 | 1.2 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | n2o [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0089
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2015 | 20 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | nox [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2020 | 15 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | nox [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2030 | 10 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | nox [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2050 | 8 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | nox [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | lower | 2020 | 10 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | nox [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | lower | 2050 | 5 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | nox [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | upper | 2020 | 30 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | nox [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | upper | 2050 | 15 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | nox [g/gj_i] | ELH_0030 | tk_env | manual_category_map | PAR_0152
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | so2 (degree of desulphuring) [] | ELH_0030 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | so2 (degree of desulphuring) [] | ELH_0030 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | so2 (degree of desulphuring) [] | ELH_0030 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 0 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | so2 (degree of desulphuring) [] | ELH_0030 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2020 | 0 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | so2 (degree of desulphuring) [] | ELH_0030 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2050 | 0 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | so2 (degree of desulphuring) [] | ELH_0030 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2020 | 0 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | so2 (degree of desulphuring) [] | ELH_0030 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2050 | 0 | gas turbine, combined cycle - back pressure - natural gas - medium | environment | so2 (degree of desulphuring) [] | ELH_0030 | tk_env | manual_category_map | PAR_0181
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2015 | 31901.1815 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0030 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2020 | 31156.8206 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0030 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2030 | 29561.7616 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0030 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2050 | 27647.6907 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0030 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | lower | 2020 | 26584.318 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0030 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | lower | 2050 | 21267.4544 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0030 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | upper | 2020 | 37218.0451 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0030 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | upper | 2050 | 31901.1815 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0030 | tk_fin | manual_category_map | PAR_0042
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | ctrl | 2015 | 1.3824 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | ctrl | 2020 | 1.3824 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | ctrl | 2030 | 1.276 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | ctrl | 2050 | 1.1697 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | lower | 2020 | 1.1697 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | lower | 2050 | 0.95704 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | upper | 2020 | 1.9141 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | upper | 2050 | 1.7014 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0093
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2015 | 1.0634 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2020 | 1.0634 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2030 | 0.95704 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2050 | 0.8507 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2020 | 0.8507 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2050 | 0.69119 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2020 | 1.4887 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2050 | 1.3292 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0104
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2015 | 0.31901 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2020 | 0.31901 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2030 | 0.31901 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2050 | 0.31901 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2020 | 0.31901 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2050 | 0.26584 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2020 | 0.42535 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2050 | 0.37218 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0115
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2015 | 4.7852 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2020 | 4.6788 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2030 | 4.4662 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2050 | 4.2535 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | lower | 2020 | 3.1901 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | lower | 2050 | 3.1901 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | upper | 2020 | 7.4436 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | upper | 2050 | 7.4436 | gas turbine, combined cycle - back pressure - natural gas - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0030 | tk_fin | manual_category_map | PAR_0201
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2015 | 2.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | cold start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2020 | 2.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | cold start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2030 | 2.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | cold start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2050 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | cold start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | lower | 2020 | 2 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | cold start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | lower | 2050 | 1.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | cold start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | upper | 2020 | 5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | cold start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | upper | 2050 | 5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | cold start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0022
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2015 | 0.4 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | minimum load (of full load) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2020 | 0.4 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | minimum load (of full load) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2030 | 0.4 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | minimum load (of full load) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2050 | 0.4 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | minimum load (of full load) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | lower | 2020 | 0.3 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | minimum load (of full load) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | lower | 2050 | 0.3 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | minimum load (of full load) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | upper | 2020 | 0.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | minimum load (of full load) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | upper | 2050 | 0.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | minimum load (of full load) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0085
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | ctrl | 2015 | 0.15 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | ctrl | 2020 | 0.15 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | ctrl | 2030 | 0.15 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | ctrl | 2050 | 0.15 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | lower | 2020 | 0.05 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | lower | 2050 | 0.05 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | upper | 2020 | 0.15 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | upper | 2050 | 0.15 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0030 | tk_reg | manual_category_map | PAR_0179
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2015 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | warm start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2020 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | warm start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2030 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | warm start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2050 | 1 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | warm start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | lower | 2020 | 0.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | warm start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | lower | 2050 | 0.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | warm start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | upper | 2020 | 1.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | warm start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0211
ELH | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | upper | 2050 | 1.5 | gas turbine, combined cycle - back pressure - natural gas - medium | regulation ability | warm start-up time [hours] | ELH_0030 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2015 | 0.9 | engine - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0024 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2020 | 0.95 | engine - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0024 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2030 | 0.99 | engine - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0024 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2050 | 1.04 | engine - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0024 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | lower | 2020 | 0.65 | engine - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0024 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | lower | 2050 | 0.65 | engine - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0024 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | upper | 2020 | 1.02 | engine - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0024 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | upper | 2050 | 1.15 | engine - back pressure - natural gas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0024 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2015 | 1 | engine - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2020 | 1 | engine - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2030 | 1 | engine - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2050 | 1 | engine - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | lower | 2020 | 0.5 | engine - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | lower | 2050 | 0.5 | engine - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | upper | 2020 | 1.5 | engine - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | upper | 2050 | 1.5 | engine - back pressure - natural gas - small | energy/technical data | construction time [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2015 | 0.44 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2020 | 0.45 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2030 | 0.47 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2050 | 0.48 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | lower | 2020 | 0.38 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | lower | 2050 | 0.42 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | upper | 2020 | 0.46 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | upper | 2050 | 0.5 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2015 | 0.46 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2020 | 0.47 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2030 | 0.48 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2050 | 0.5 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | lower | 2020 | 0.4 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | lower | 2050 | 0.44 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | upper | 2020 | 0.48 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | upper | 2050 | 0.52 | engine - back pressure - natural gas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0024 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2015 | 0.03 | engine - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0024 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2020 | 0.03 | engine - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0024 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2030 | 0.03 | engine - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0024 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2050 | 0.03 | engine - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0024 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | lower | 2020 | 0.02 | engine - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0024 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | lower | 2050 | 0.02 | engine - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0024 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | upper | 2020 | 0.05 | engine - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0024 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | upper | 2050 | 0.05 | engine - back pressure - natural gas - small | energy/technical data | forced outage [] | ELH_0024 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 1 | engine - back pressure - natural gas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0071
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 1 | engine - back pressure - natural gas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0071
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 10 | engine - back pressure - natural gas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0071
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 10 | engine - back pressure - natural gas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0071
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2015 | 0.8 | engine - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0024 | tk_etd | manual_category_map | PAR_0168
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2020 | 0.8 | engine - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0024 | tk_etd | manual_category_map | PAR_0168
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2030 | 0.8 | engine - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0024 | tk_etd | manual_category_map | PAR_0168
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2050 | 0.8 | engine - back pressure - natural gas - small | energy/technical data | planned outage [weeks per year] | ELH_0024 | tk_etd | manual_category_map | PAR_0168
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.04 | engine - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.04 | engine - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.04 | engine - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.03 | engine - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.03 | engine - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.03 | engine - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.05 | engine - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.04 | engine - back pressure - natural gas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0024 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2015 | 25 | engine - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2020 | 25 | engine - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2030 | 25 | engine - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2050 | 25 | engine - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | lower | 2020 | 25 | engine - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | lower | 2050 | 25 | engine - back pressure - natural gas - small | energy/technical data | technical lifetime [years] | ELH_0024 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2015 | 315 | engine - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 315 | engine - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 280 | engine - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 250 | engine - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2020 | 300 | engine - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 250 | engine - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2020 | 400 | engine - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 350 | engine - back pressure - natural gas - small | environment | ch4 [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | H |  | ctrl | 2015 | 0.6 | engine - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0089
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | H |  | ctrl | 2020 | 0.6 | engine - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0089
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | H |  | ctrl | 2030 | 0.6 | engine - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0089
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | H |  | ctrl | 2050 | 0.6 | engine - back pressure - natural gas - small | environment | n2o [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0089
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2015 | 75 | engine - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 60 | engine - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 60 | engine - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 60 | engine - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2020 | 50 | engine - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 50 | engine - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2020 | 100 | engine - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 100 | engine - back pressure - natural gas - small | environment | nox [g/gj_i] | ELH_0024 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | ctrl | 2015 | 0 | engine - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0024 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | ctrl | 2020 | 0 | engine - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0024 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | ctrl | 2030 | 0 | engine - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0024 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | ctrl | 2050 | 0 | engine - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0024 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | lower | 2020 | 0 | engine - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0024 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | lower | 2050 | 0 | engine - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0024 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | upper | 2020 | 0 | engine - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0024 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | upper | 2050 | 0 | engine - back pressure - natural gas - small | environment | so2 (degree of desulphuring) [] | ELH_0024 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2015 | 10633.7272 | engine - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0024 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2020 | 10367.884 | engine - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0024 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2030 | 9889.3663 | engine - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0024 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2050 | 9038.6681 | engine - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0024 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | lower | 2020 | 7443.609 | engine - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0024 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | lower | 2050 | 6380.2363 | engine - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0024 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | upper | 2020 | 21267.4544 | engine - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0024 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | upper | 2050 | 15950.5908 | engine - back pressure - natural gas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0024 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2015 | 1.0634 | engine - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2020 | 1.0102 | engine - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2030 | 0.95704 | engine - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2050 | 0.90387 | engine - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | lower | 2020 | 0.95704 | engine - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | lower | 2050 | 0.8507 | engine - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | upper | 2020 | 1.1697 | engine - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | upper | 2050 | 1.1697 | engine - back pressure - natural gas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2015 | 0.69119 | engine - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2020 | 0.63802 | engine - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2030 | 0.58485 | engine - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2050 | 0.58485 | engine - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | lower | 2020 | 0 | engine - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | lower | 2050 | 0 | engine - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | upper | 2020 | 0 | engine - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | upper | 2050 | 0 | engine - back pressure - natural gas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2015 | 0.37218 | engine - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2020 | 0.37218 | engine - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2030 | 0.37218 | engine - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2050 | 0.31901 | engine - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | lower | 2020 | 0 | engine - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | lower | 2050 | 0 | engine - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | upper | 2020 | 0 | engine - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | upper | 2050 | 0 | engine - back pressure - natural gas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2015 | 5.7422 | engine - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2020 | 5.7422 | engine - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2030 | 5.4232 | engine - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2050 | 5.2105 | engine - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | lower | 2020 | 4.2535 | engine - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | lower | 2050 | 4.2535 | engine - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | upper | 2020 | 12.7605 | engine - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | upper | 2050 | 10.6337 | engine - back pressure - natural gas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0024 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2015 | 0.3 | engine - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2020 | 0.3 | engine - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2030 | 0.3 | engine - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2050 | 0.3 | engine - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | lower | 2020 | 0.2 | engine - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | lower | 2050 | 0.2 | engine - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | upper | 2020 | 0.4 | engine - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | upper | 2050 | 0.4 | engine - back pressure - natural gas - small | regulation ability | cold start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2015 | 0.5 | engine - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2020 | 0.5 | engine - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2030 | 0.5 | engine - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2050 | 0.5 | engine - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | lower | 2020 | 0.3 | engine - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | lower | 2050 | 0.25 | engine - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | upper | 2020 | 0.5 | engine - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | upper | 2050 | 0.5 | engine - back pressure - natural gas - small | regulation ability | minimum load (of full load) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | ctrl | 2015 | 0.25 | engine - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | ctrl | 2020 | 0.3 | engine - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | ctrl | 2030 | 0.35 | engine - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | ctrl | 2050 | 0.5 | engine - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | lower | 2020 | 0.1 | engine - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | lower | 2050 | 0.25 | engine - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | upper | 2020 | 0.4 | engine - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | upper | 2050 | 1 | engine - back pressure - natural gas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | ctrl | 2015 | 0.25 | engine - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | ctrl | 2020 | 0.3 | engine - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | ctrl | 2030 | 0.4 | engine - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | ctrl | 2050 | 0.5 | engine - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | lower | 2020 | 0.2 | engine - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | lower | 2050 | 0.25 | engine - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | upper | 2020 | 1 | engine - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | upper | 2050 | 1 | engine - back pressure - natural gas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0024 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2015 | 0.05 | engine - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2020 | 0.05 | engine - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2030 | 0.05 | engine - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2050 | 0.05 | engine - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | lower | 2020 | 0.01 | engine - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | lower | 2050 | 0.01 | engine - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | upper | 2020 | 0.15 | engine - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | upper | 2050 | 0.15 | engine - back pressure - natural gas - small | regulation ability | warm start-up time [hours] | ELH_0024 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2015 | 0.82 | engine - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0023 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2020 | 0.86 | engine - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0023 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2030 | 0.92 | engine - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0023 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2050 | 1 | engine - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0023 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | lower | 2020 | 0.59 | engine - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0023 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | lower | 2050 | 0.75 | engine - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0023 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | upper | 2020 | 0.96 | engine - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0023 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | upper | 2050 | 1.1 | engine - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0023 | tk_etd | manual_category_map | PAR_0015
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2015 | 1 | engine - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2020 | 1 | engine - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2030 | 1 | engine - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2050 | 1 | engine - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | lower | 2020 | 0.5 | engine - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | lower | 2050 | 0.5 | engine - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | upper | 2020 | 1.5 | engine - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | upper | 2050 | 1.5 | engine - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0026
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2015 | 0.4 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2020 | 0.41 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2030 | 0.43 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2050 | 0.45 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | lower | 2020 | 0.36 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | lower | 2050 | 0.4 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | upper | 2020 | 0.42 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | upper | 2050 | 0.46 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0034
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2015 | 0.42 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2020 | 0.43 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2030 | 0.45 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2050 | 0.47 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | lower | 2020 | 0.38 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | lower | 2050 | 0.42 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | upper | 2020 | 0.44 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | upper | 2050 | 0.48 | engine - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0023 | tk_etd | manual_category_map | PAR_0036
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2015 | 0.03 | engine - back pressure - biogas - small | energy/technical data | forced outage [] | ELH_0023 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2020 | 0.03 | engine - back pressure - biogas - small | energy/technical data | forced outage [] | ELH_0023 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2030 | 0.03 | engine - back pressure - biogas - small | energy/technical data | forced outage [] | ELH_0023 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2050 | 0.03 | engine - back pressure - biogas - small | energy/technical data | forced outage [] | ELH_0023 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | lower | 2020 | 0.02 | engine - back pressure - biogas - small | energy/technical data | forced outage [] | ELH_0023 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | lower | 2050 | 0.02 | engine - back pressure - biogas - small | energy/technical data | forced outage [] | ELH_0023 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | upper | 2020 | 0.05 | engine - back pressure - biogas - small | energy/technical data | forced outage [] | ELH_0023 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | upper | 2050 | 0.05 | engine - back pressure - biogas - small | energy/technical data | forced outage [] | ELH_0023 | tk_etd | manual_category_map | PAR_0065
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 1 | engine - back pressure - biogas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0071
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 1 | engine - back pressure - biogas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0071
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 10 | engine - back pressure - biogas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0071
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 10 | engine - back pressure - biogas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0071
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2015 | 1 | engine - back pressure - biogas - small | energy/technical data | planned outage [weeks per year] | ELH_0023 | tk_etd | manual_category_map | PAR_0168
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2020 | 1 | engine - back pressure - biogas - small | energy/technical data | planned outage [weeks per year] | ELH_0023 | tk_etd | manual_category_map | PAR_0168
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2030 | 1 | engine - back pressure - biogas - small | energy/technical data | planned outage [weeks per year] | ELH_0023 | tk_etd | manual_category_map | PAR_0168
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2050 | 1 | engine - back pressure - biogas - small | energy/technical data | planned outage [weeks per year] | ELH_0023 | tk_etd | manual_category_map | PAR_0168
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.04 | engine - back pressure - biogas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.04 | engine - back pressure - biogas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.04 | engine - back pressure - biogas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.03 | engine - back pressure - biogas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.03 | engine - back pressure - biogas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.03 | engine - back pressure - biogas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.05 | engine - back pressure - biogas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.05 | engine - back pressure - biogas - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0023 | tk_etd | manual_category_map | PAR_0188
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2015 | 25 | engine - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2020 | 25 | engine - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2030 | 25 | engine - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2050 | 25 | engine - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | lower | 2020 | 25 | engine - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | lower | 2050 | 25 | engine - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0023 | tk_etd | manual_category_map | PAR_0198
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2015 | 300 | engine - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 300 | engine - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 300 | engine - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 300 | engine - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2020 | 300 | engine - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 300 | engine - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2020 | 400 | engine - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 400 | engine - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0018
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J |  | ctrl | 2015 | 1 | engine - back pressure - biogas - small | environment | n2o [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0089
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J |  | ctrl | 2020 | 1 | engine - back pressure - biogas - small | environment | n2o [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0089
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J |  | ctrl | 2030 | 1 | engine - back pressure - biogas - small | environment | n2o [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0089
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J |  | ctrl | 2050 | 1 | engine - back pressure - biogas - small | environment | n2o [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0089
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2015 | 100 | engine - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 100 | engine - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 100 | engine - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 100 | engine - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2020 | 90 | engine - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 90 | engine - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2020 | 120 | engine - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 120 | engine - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0023 | tk_env | manual_category_map | PAR_0152
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  | K | 8 | lower | 2020 | 0 | engine - back pressure - biogas - small | environment | so2 (degree of desulphuring) [] | ELH_0023 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  | K | 8 | lower | 2050 | 0 | engine - back pressure - biogas - small | environment | so2 (degree of desulphuring) [] | ELH_0023 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  | K | 8 | upper | 2020 | 0.999 | engine - back pressure - biogas - small | environment | so2 (degree of desulphuring) [] | ELH_0023 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  | K | 8 | upper | 2050 | 0.999 | engine - back pressure - biogas - small | environment | so2 (degree of desulphuring) [] | ELH_0023 | tk_env | manual_category_map | PAR_0181
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2015 | 10633.7272 | engine - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0023 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2020 | 10367.884 | engine - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0023 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2030 | 9889.3663 | engine - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0023 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2050 | 9038.6681 | engine - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0023 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | lower | 2020 | 7443.609 | engine - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0023 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | lower | 2050 | 6380.2363 | engine - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0023 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | upper | 2020 | 21267.4544 | engine - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0023 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | upper | 2050 | 15950.5908 | engine - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0023 | tk_fin | manual_category_map | PAR_0042
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2015 | 1.0634 | engine - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2020 | 1.0102 | engine - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2030 | 0.95704 | engine - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2050 | 0.90387 | engine - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | lower | 2020 | 0.8507 | engine - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | lower | 2050 | 0.8507 | engine - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | upper | 2020 | 1.276 | engine - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | upper | 2050 | 1.276 | engine - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0093
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2015 | 0.69119 | engine - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2020 | 0.63802 | engine - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2030 | 0.58485 | engine - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2050 | 0.58485 | engine - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | lower | 2020 | 0 | engine - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | lower | 2050 | 0 | engine - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | upper | 2020 | 0 | engine - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | upper | 2050 | 0 | engine - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0104
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2015 | 0.37218 | engine - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2020 | 0.37218 | engine - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2030 | 0.37218 | engine - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2050 | 0.31901 | engine - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | lower | 2020 | 0 | engine - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | lower | 2050 | 0 | engine - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | upper | 2020 | 0 | engine - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | upper | 2050 | 0 | engine - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0115
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2015 | 8.507 | engine - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2020 | 7.9753 | engine - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2030 | 7.4436 | engine - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2050 | 6.3802 | engine - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | lower | 2020 | 6.3802 | engine - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | lower | 2050 | 4.2535 | engine - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | upper | 2020 | 13.8238 | engine - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | upper | 2050 | 12.7605 | engine - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0023 | tk_fin | manual_category_map | PAR_0201
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2015 | 0.3 | engine - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2020 | 0.3 | engine - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2030 | 0.3 | engine - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2050 | 0.3 | engine - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | lower | 2020 | 0.2 | engine - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | lower | 2050 | 0.2 | engine - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | upper | 2020 | 0.4 | engine - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | upper | 2050 | 0.4 | engine - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0022
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2015 | 0.5 | engine - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2020 | 0.5 | engine - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2030 | 0.5 | engine - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2050 | 0.5 | engine - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | lower | 2020 | 0.3 | engine - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | lower | 2050 | 0.25 | engine - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | upper | 2020 | 0.5 | engine - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | upper | 2050 | 0.5 | engine - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0085
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | ctrl | 2015 | 0.25 | engine - back pressure - biogas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | ctrl | 2020 | 0.3 | engine - back pressure - biogas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | ctrl | 2030 | 0.4 | engine - back pressure - biogas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | ctrl | 2050 | 0.5 | engine - back pressure - biogas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | lower | 2020 | 0.1 | engine - back pressure - biogas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | lower | 2050 | 0.25 | engine - back pressure - biogas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | upper | 2020 | 0.4 | engine - back pressure - biogas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | upper | 2050 | 1 | engine - back pressure - biogas - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0171
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | ctrl | 2015 | 0.25 | engine - back pressure - biogas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | ctrl | 2020 | 0.3 | engine - back pressure - biogas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | ctrl | 2030 | 0.4 | engine - back pressure - biogas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | ctrl | 2050 | 0.5 | engine - back pressure - biogas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | lower | 2020 | 0.2 | engine - back pressure - biogas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | lower | 2050 | 0.25 | engine - back pressure - biogas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | upper | 2020 | 1 | engine - back pressure - biogas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | upper | 2050 | 1 | engine - back pressure - biogas - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0023 | tk_reg | manual_category_map | PAR_0179
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2015 | 0.05 | engine - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2020 | 0.05 | engine - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2030 | 0.05 | engine - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2050 | 0.05 | engine - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | lower | 2020 | 0.01 | engine - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | lower | 2050 | 0.01 | engine - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | upper | 2020 | 0.15 | engine - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0211
ELH | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | upper | 2050 | 0.15 | engine - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0023 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2015 | 0.029099 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2020 | 0.029099 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2030 | 0.029215 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2050 | 0.02911 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2020 | 0.021471 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2050 | 0.017177 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2020 | 0.031962 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2050 | 0.032382 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 0.3 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 0.3 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 0.31 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 0.32 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 0.27 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 0.27 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 0.32 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 0.35 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 3 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 3 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 3 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 3 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2.5 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3.5 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3.5 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 1 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 1 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0074 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.22357 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.22357 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.22886 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.23712 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.19 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.19 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.25 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.27 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.23534 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.23534 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.24091 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.2496 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.21 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.21 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.26 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.28 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0074 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0074 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0074 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0074 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0074 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0074 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0074 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0074 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0074 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 51.77 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 51.77 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 53 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 54.91 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2020 | 46.98 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2050 | 46.98 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2020 | 56.44 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2050 | 60.65 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 2.5 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0074 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 2.38 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0074 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 2.15 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0074 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 1.76 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0074 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.02 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0074 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.32 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0074 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 2.73 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0074 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 2.2 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0074 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.77 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.77 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.75 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.73 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.66 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.55 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.89 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.91 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0074 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | waste chp, 40/80 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0074 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3 | waste chp, 40/80 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0 | waste chp, 40/80 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0 | waste chp, 40/80 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2 | waste chp, 40/80 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1 | waste chp, 40/80 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0 | waste chp, 40/80 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3 | waste chp, 40/80 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80 | waste chp, 40/80 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60 | waste chp, 40/80 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 20 | waste chp, 40/80 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10 | waste chp, 40/80 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10 | waste chp, 40/80 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10 | waste chp, 40/80 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60 | waste chp, 40/80 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60 | waste chp, 40/80 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3 | waste chp, 40/80 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3 | waste chp, 40/80 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3 | waste chp, 40/80 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3 | waste chp, 40/80 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2 | waste chp, 40/80 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0074 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792 | waste chp, 40/80 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0074 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792 | waste chp, 40/80 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0074 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792 | waste chp, 40/80 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0074 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792 | waste chp, 40/80 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0074 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962 | waste chp, 40/80 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0074 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481 | waste chp, 40/80 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0074 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896 | waste chp, 40/80 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0074 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896 | waste chp, 40/80 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0074 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2015 | 243512.3524 | waste chp, 40/80 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0074 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2020 | 197787.3255 | waste chp, 40/80 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0074 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2030 | 185026.8529 | waste chp, 40/80 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0074 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2050 | 157379.1623 | waste chp, 40/80 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0074 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2020 | 168012.8894 | waste chp, 40/80 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0074 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2050 | 115907.6263 | waste chp, 40/80 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0074 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2020 | 231815.2525 | waste chp, 40/80 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0074 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2050 | 195660.5801 | waste chp, 40/80 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0074 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 8.4538 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 8.2518 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 7.8477 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 6.8694 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 7.0076 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 5.0191 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 9.6661 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 8.5389 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 5.0936 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 4.9766 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 4.7958 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 4.211 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 4.2216 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 3.02 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 5.9017 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 5.2105 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2015 | 3.3603 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2020 | 3.2752 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2030 | 3.0412 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2050 | 2.6584 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2020 | 2.786 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2050 | 1.9885 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2020 | 3.7643 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2050 | 3.3177 | waste chp, 40/80 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2015 | 26.5737 | waste chp, 40/80 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2020 | 26.5737 | waste chp, 40/80 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2030 | 25.9782 | waste chp, 40/80 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2050 | 25.0956 | waste chp, 40/80 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2020 | 22.6073 | waste chp, 40/80 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2050 | 18.8642 | waste chp, 40/80 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2020 | 30.6251 | waste chp, 40/80 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2050 | 31.3589 | waste chp, 40/80 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0074 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2015 | 0.2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2020 | 0.2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2030 | 0.2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2050 | 0.2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2020 | 0.2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2050 | 0.2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2020 | 0.2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2050 | 0.2 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2015 | 0.05 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2020 | 0.05 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2030 | 0.05 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2050 | 0.05 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2020 | 0.05 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2050 | 0.05 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2020 | 0.05 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2050 | 0.05 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2015 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2020 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2030 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2050 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2020 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2050 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2020 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2050 | 0.1 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0074 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 0.5 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 0.5 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 0.5 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 0.5 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 0.5 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 0.5 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 0.5 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 0.5 | waste chp, 40/80 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0074 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.041506 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.041506 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.040149 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.037398 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.01 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.06 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.06 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2015 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0074 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2020 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0074 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2030 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0074 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2050 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0074 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2020 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0074 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2050 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0074 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0074 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0074 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 57422.1267 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 46682.0623 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 44555.3169 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 39344.7905 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 39663.8024 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 28817.4006 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 54551.0204 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 48915.145 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 21.1292 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 17.1735 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 16.4078 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 14.4725 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 14.6001 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 10.6231 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 20.0658 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 18.0135 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0074 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2015 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0074 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0074 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2030 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0074 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0074 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0074 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0074 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2020 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0074 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2050 | 1 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0074 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.80185 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.80185 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.79888 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.79566 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.76 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.73 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.85 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.87 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.79009 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.79009 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.78683 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.78318 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.74 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.71 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.84 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.86 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0074 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 74.69 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0074 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 74.69 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0074 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 74.69 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0074 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 74.69 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0074 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 74.69 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0074 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 74.69 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0074 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 74.69 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0074 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 74.69 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0074 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.9885 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.946 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.8928 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.712 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.6482 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.2548 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.2756 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.1267 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 733.7272 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 712.4597 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 691.1923 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 627.3899 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 606.1224 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 457.2503 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 840.0644 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 786.8958 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.2016 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.1697 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.1591 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.0527 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 0.99957 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 0.75499 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.393 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.2973 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 0.7869 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.76563 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.73373 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.65929 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.65929 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.49979 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 0.8826 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 0.82943 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.4176 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.4176 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.4282 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.4495 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.6741 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.8664 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.2356 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 23.0539 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.11697 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.11697 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11697 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.1276 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.10634 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.10634 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.14887 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.15951 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2015 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0074 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2020 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0074 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2030 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0074 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2050 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0074 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | lower | 2020 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0074 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | lower | 2050 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0074 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | upper | 2020 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0074 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | upper | 2050 | 0 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0074 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 6.2526 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 6.2526 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 6.2526 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 6.2633 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 5.3169 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 4.7107 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 7.2097 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 7.8264 | waste chp, 40/80 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0074 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2015 | 0.029566 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2020 | 0.029566 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2030 | 0.029667 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2050 | 0.029534 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2020 | 0.021847 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2050 | 0.017478 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2020 | 0.032244 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2050 | 0.032647 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2015 | 0.28 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0015
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2020 | 0.28 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0015
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2030 | 0.29 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0015
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2050 | 0.3 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0015
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | lower | 2020 | 0.25 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0015
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | lower | 2050 | 0.25 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0015
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | upper | 2020 | 0.31 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0015
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | upper | 2050 | 0.34 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0015
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 3 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 3 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 3 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 3 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2.5 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3.5 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3.5 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | construction time [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2015 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0028
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0028
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2030 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0028
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0028
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | lower | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0028
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | lower | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0028
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | upper | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0028
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | upper | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0075 | tk_etd | manual_category_map | PAR_0028
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.20215 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.20215 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.20813 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.21654 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.17 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.17 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.23 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.25 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.21279 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.21279 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.21908 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.22793 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.19 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.19 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.24 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.26 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0075 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0075 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0075 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0075 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0075 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0075 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0075 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0075 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | forced outage [] | ELH_0075 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 46.81 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 46.81 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 48.2 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 50.15 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2020 | 42.06 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2050 | 42.06 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2020 | 51.61 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2050 | 55.88 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 2.5 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0075 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 2.38 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0075 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 2.15 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0075 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 1.76 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0075 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.02 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0075 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.32 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0075 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 2.73 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0075 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 2.2 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | planned outage [weeks per year] | ELH_0075 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.85 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.85 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.83 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.8 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.73 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.6 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.98 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0075 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | waste chp, 50/100 degree - back pressure - waste - large | energy/technical data | technical lifetime [years] | ELH_0075 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3 | waste chp, 50/100 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0 | waste chp, 50/100 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0 | waste chp, 50/100 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | environment | ch4 [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2 | waste chp, 50/100 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1 | waste chp, 50/100 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0 | waste chp, 50/100 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3 | waste chp, 50/100 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | environment | n2o [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80 | waste chp, 50/100 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60 | waste chp, 50/100 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 20 | waste chp, 50/100 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10 | waste chp, 50/100 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10 | waste chp, 50/100 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10 | waste chp, 50/100 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60 | waste chp, 50/100 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60 | waste chp, 50/100 degree - back pressure - waste - large | environment | nox [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3 | waste chp, 50/100 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3 | waste chp, 50/100 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3 | waste chp, 50/100 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3 | waste chp, 50/100 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2 | waste chp, 50/100 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | environment | particles [g/gj_i] | ELH_0075 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792 | waste chp, 50/100 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0075 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792 | waste chp, 50/100 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0075 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792 | waste chp, 50/100 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0075 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792 | waste chp, 50/100 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0075 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962 | waste chp, 50/100 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0075 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481 | waste chp, 50/100 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0075 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896 | waste chp, 50/100 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0075 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896 | waste chp, 50/100 degree - back pressure - waste - large | environment | so2 (degree of desulphuring) [] | ELH_0075 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2015 | 270096.6704 | waste chp, 50/100 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0075 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2020 | 219054.7799 | waste chp, 50/100 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0075 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2030 | 203104.1891 | waste chp, 50/100 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0075 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2050 | 172266.3803 | waste chp, 50/100 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0075 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2020 | 186090.2257 | waste chp, 50/100 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0075 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2050 | 126541.3534 | waste chp, 50/100 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0075 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2020 | 256272.825 | waste chp, 50/100 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0075 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2050 | 214801.289 | waste chp, 50/100 degree - back pressure - waste - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0075 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 9.3577 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 9.1237 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 8.624 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 7.518 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 7.752 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 5.4976 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 10.6975 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 9.347 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 5.6359 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 5.4976 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 5.2743 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 4.6044 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 4.6788 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 3.3071 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 6.5291 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 5.7103 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2015 | 3.7112 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2020 | 3.6261 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2030 | 3.3496 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2050 | 2.9136 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2020 | 3.0838 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2050 | 2.1799 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2020 | 4.1684 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2050 | 3.6367 | waste chp, 50/100 degree - back pressure - waste - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2015 | 29.0088 | waste chp, 50/100 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2020 | 29.0088 | waste chp, 50/100 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2030 | 28.2006 | waste chp, 50/100 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2050 | 27.1585 | waste chp, 50/100 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2020 | 24.5745 | waste chp, 50/100 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2050 | 20.2466 | waste chp, 50/100 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2020 | 33.7089 | waste chp, 50/100 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2050 | 34.1874 | waste chp, 50/100 degree - back pressure - waste - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0075 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | cold start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2015 | 0.2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2020 | 0.2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2030 | 0.2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2050 | 0.2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2020 | 0.2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2050 | 0.2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2020 | 0.2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2050 | 0.2 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | minimum load (of full load) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2015 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2020 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2030 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2050 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2020 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2050 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2020 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2050 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2015 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2020 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2030 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2050 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2020 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2050 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2020 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2050 | 0.1 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0075 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 0.5 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 0.5 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 0.5 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 0.5 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 0.5 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 0.5 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 0.5 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 0.5 | waste chp, 50/100 degree - back pressure - waste - large | regulation ability | warm start-up time [hours] | ELH_0075 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.10038 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.10038 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.097086 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.090423 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.04 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.04 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.12 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.12 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2015 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0075 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2020 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0075 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2030 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0075 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2050 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0075 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2020 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0075 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2050 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0075 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0075 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | combustion air humidification | ELH_0075 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 57422.1267 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 46682.0623 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 44555.3169 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 39344.7905 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 39663.8024 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 28817.4006 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 54551.0204 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 48915.145 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 21.1292 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 17.1735 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 16.4078 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 14.4725 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 14.6001 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 10.6231 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 20.0658 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 18.0135 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0075 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2015 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0075 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0075 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2030 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0075 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0075 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0075 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0075 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2020 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0075 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2050 | 1 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | flue gas condensation | ELH_0075 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.76349 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.76349 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.76185 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.76254 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.72 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.7 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.85 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.86 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.75285 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.75285 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.7509 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.75114 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.7 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.68 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.84 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.85 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0075 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 74.69 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0075 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 74.69 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0075 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 74.69 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0075 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 74.69 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0075 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 74.69 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0075 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 74.69 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0075 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 74.69 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0075 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 74.69 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | incineration capacity [t_i/h] | ELH_0075 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.9885 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.946 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.8928 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.712 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.6482 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.2548 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.2756 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.1267 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 733.7272 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 712.4597 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 691.1923 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 627.3899 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 606.1224 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 457.2503 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 840.0644 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 786.8958 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.2016 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.1697 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.1591 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.0527 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 0.99957 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 0.75499 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.393 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.2973 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 0.7869 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.76563 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.73373 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.65929 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.65929 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.49979 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 0.8826 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 0.82943 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.1837 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.1837 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.1943 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.2368 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.4083 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.6005 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.1292 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 22.9582 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.03 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.03 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.04 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.05 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.01 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.11 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.11 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2015 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0075 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2020 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0075 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2030 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0075 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2050 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0075 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | lower | 2020 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0075 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | lower | 2050 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0075 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | upper | 2020 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0075 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | upper | 2050 | 0 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | steam reheat | ELH_0075 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 6.1676 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 6.1676 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 6.1782 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 6.1888 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 5.2318 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 4.615 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 7.1671 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 7.7945 | waste chp, 50/100 degree - back pressure - waste - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0075 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2015 | 0.029101 | waste chp - back pressure - waste - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2020 | 0.029101 | waste chp - back pressure - waste - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2030 | 0.029217 | waste chp - back pressure - waste - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2050 | 0.029112 | waste chp - back pressure - waste - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2020 | 0.021472 | waste chp - back pressure - waste - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2050 | 0.017178 | waste chp - back pressure - waste - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2020 | 0.031965 | waste chp - back pressure - waste - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2050 | 0.032684 | waste chp - back pressure - waste - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 0.3 | waste chp - back pressure - waste - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 0.3 | waste chp - back pressure - waste - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 0.3 | waste chp - back pressure - waste - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 0.31 | waste chp - back pressure - waste - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 0.27 | waste chp - back pressure - waste - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 0.27 | waste chp - back pressure - waste - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 0.32 | waste chp - back pressure - waste - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 0.35 | waste chp - back pressure - waste - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5 | waste chp - back pressure - waste - medium | energy/technical data | construction time [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5 | waste chp - back pressure - waste - medium | energy/technical data | construction time [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5 | waste chp - back pressure - waste - medium | energy/technical data | construction time [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5 | waste chp - back pressure - waste - medium | energy/technical data | construction time [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2 | waste chp - back pressure - waste - medium | energy/technical data | construction time [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5 | waste chp - back pressure - waste - medium | energy/technical data | construction time [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3 | waste chp - back pressure - waste - medium | energy/technical data | construction time [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3 | waste chp - back pressure - waste - medium | energy/technical data | construction time [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 1 | waste chp - back pressure - waste - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 1 | waste chp - back pressure - waste - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 1 | waste chp - back pressure - waste - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 1 | waste chp - back pressure - waste - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 1 | waste chp - back pressure - waste - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 1 | waste chp - back pressure - waste - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 1 | waste chp - back pressure - waste - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 1 | waste chp - back pressure - waste - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0072 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.221 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.221 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.22599 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.23383 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.19 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.19 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.25 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.26 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.23263 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.23263 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.23788 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.24614 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2020 | 0.21 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2050 | 0.21 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2020 | 0.26 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2050 | 0.28 | waste chp - back pressure - waste - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0072 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01 | waste chp - back pressure - waste - medium | energy/technical data | forced outage [] | ELH_0072 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01 | waste chp - back pressure - waste - medium | energy/technical data | forced outage [] | ELH_0072 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01 | waste chp - back pressure - waste - medium | energy/technical data | forced outage [] | ELH_0072 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01 | waste chp - back pressure - waste - medium | energy/technical data | forced outage [] | ELH_0072 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01 | waste chp - back pressure - waste - medium | energy/technical data | forced outage [] | ELH_0072 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01 | waste chp - back pressure - waste - medium | energy/technical data | forced outage [] | ELH_0072 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01 | waste chp - back pressure - waste - medium | energy/technical data | forced outage [] | ELH_0072 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01 | waste chp - back pressure - waste - medium | energy/technical data | forced outage [] | ELH_0072 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 18.61 | waste chp - back pressure - waste - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 18.61 | waste chp - back pressure - waste - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 19.03 | waste chp - back pressure - waste - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 19.69 | waste chp - back pressure - waste - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2020 | 16.91 | waste chp - back pressure - waste - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2050 | 16.91 | waste chp - back pressure - waste - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2020 | 20.24 | waste chp - back pressure - waste - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2050 | 21.66 | waste chp - back pressure - waste - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 3 | waste chp - back pressure - waste - medium | energy/technical data | planned outage [weeks per year] | ELH_0072 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 2.85 | waste chp - back pressure - waste - medium | energy/technical data | planned outage [weeks per year] | ELH_0072 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 2.58 | waste chp - back pressure - waste - medium | energy/technical data | planned outage [weeks per year] | ELH_0072 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 2.11 | waste chp - back pressure - waste - medium | energy/technical data | planned outage [weeks per year] | ELH_0072 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.43 | waste chp - back pressure - waste - medium | energy/technical data | planned outage [weeks per year] | ELH_0072 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.58 | waste chp - back pressure - waste - medium | energy/technical data | planned outage [weeks per year] | ELH_0072 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 3.28 | waste chp - back pressure - waste - medium | energy/technical data | planned outage [weeks per year] | ELH_0072 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 2.64 | waste chp - back pressure - waste - medium | energy/technical data | planned outage [weeks per year] | ELH_0072 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 1.61 | waste chp - back pressure - waste - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 1.61 | waste chp - back pressure - waste - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 1.58 | waste chp - back pressure - waste - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 1.52 | waste chp - back pressure - waste - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 1.37 | waste chp - back pressure - waste - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 1.14 | waste chp - back pressure - waste - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 1.85 | waste chp - back pressure - waste - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 1.9 | waste chp - back pressure - waste - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0072 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | waste chp - back pressure - waste - medium | energy/technical data | technical lifetime [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | waste chp - back pressure - waste - medium | energy/technical data | technical lifetime [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | waste chp - back pressure - waste - medium | energy/technical data | technical lifetime [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | waste chp - back pressure - waste - medium | energy/technical data | technical lifetime [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | waste chp - back pressure - waste - medium | energy/technical data | technical lifetime [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | waste chp - back pressure - waste - medium | energy/technical data | technical lifetime [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | waste chp - back pressure - waste - medium | energy/technical data | technical lifetime [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | waste chp - back pressure - waste - medium | energy/technical data | technical lifetime [years] | ELH_0072 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3 | waste chp - back pressure - waste - medium | environment | ch4 [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1 | waste chp - back pressure - waste - medium | environment | ch4 [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1 | waste chp - back pressure - waste - medium | environment | ch4 [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1 | waste chp - back pressure - waste - medium | environment | ch4 [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0 | waste chp - back pressure - waste - medium | environment | ch4 [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0 | waste chp - back pressure - waste - medium | environment | ch4 [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1 | waste chp - back pressure - waste - medium | environment | ch4 [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1 | waste chp - back pressure - waste - medium | environment | ch4 [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2 | waste chp - back pressure - waste - medium | environment | n2o [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1 | waste chp - back pressure - waste - medium | environment | n2o [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1 | waste chp - back pressure - waste - medium | environment | n2o [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1 | waste chp - back pressure - waste - medium | environment | n2o [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1 | waste chp - back pressure - waste - medium | environment | n2o [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0 | waste chp - back pressure - waste - medium | environment | n2o [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3 | waste chp - back pressure - waste - medium | environment | n2o [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste chp - back pressure - waste - medium | environment | n2o [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80 | waste chp - back pressure - waste - medium | environment | nox [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60 | waste chp - back pressure - waste - medium | environment | nox [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40 | waste chp - back pressure - waste - medium | environment | nox [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10 | waste chp - back pressure - waste - medium | environment | nox [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10 | waste chp - back pressure - waste - medium | environment | nox [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10 | waste chp - back pressure - waste - medium | environment | nox [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60 | waste chp - back pressure - waste - medium | environment | nox [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60 | waste chp - back pressure - waste - medium | environment | nox [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3 | waste chp - back pressure - waste - medium | environment | particles [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3 | waste chp - back pressure - waste - medium | environment | particles [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3 | waste chp - back pressure - waste - medium | environment | particles [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3 | waste chp - back pressure - waste - medium | environment | particles [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1 | waste chp - back pressure - waste - medium | environment | particles [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1 | waste chp - back pressure - waste - medium | environment | particles [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2 | waste chp - back pressure - waste - medium | environment | particles [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste chp - back pressure - waste - medium | environment | particles [g/gj_i] | ELH_0072 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792 | waste chp - back pressure - waste - medium | environment | so2 (degree of desulphuring) [] | ELH_0072 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792 | waste chp - back pressure - waste - medium | environment | so2 (degree of desulphuring) [] | ELH_0072 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792 | waste chp - back pressure - waste - medium | environment | so2 (degree of desulphuring) [] | ELH_0072 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792 | waste chp - back pressure - waste - medium | environment | so2 (degree of desulphuring) [] | ELH_0072 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962 | waste chp - back pressure - waste - medium | environment | so2 (degree of desulphuring) [] | ELH_0072 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481 | waste chp - back pressure - waste - medium | environment | so2 (degree of desulphuring) [] | ELH_0072 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896 | waste chp - back pressure - waste - medium | environment | so2 (degree of desulphuring) [] | ELH_0072 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896 | waste chp - back pressure - waste - medium | environment | so2 (degree of desulphuring) [] | ELH_0072 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2015 | 316885.07 | waste chp - back pressure - waste - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0072 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2020 | 278603.6521 | waste chp - back pressure - waste - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0072 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2030 | 260526.3159 | waste chp - back pressure - waste - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0072 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2050 | 222244.8981 | waste chp - back pressure - waste - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0072 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2020 | 237132.1161 | waste chp - back pressure - waste - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0072 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2050 | 163759.3986 | waste chp - back pressure - waste - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0072 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2020 | 325392.0517 | waste chp - back pressure - waste - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0072 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2050 | 276476.9067 | waste chp - back pressure - waste - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0072 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 9.8362 | waste chp - back pressure - waste - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 9.5916 | waste chp - back pressure - waste - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 9.145 | waste chp - back pressure - waste - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 8.0178 | waste chp - back pressure - waste - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 8.1561 | waste chp - back pressure - waste - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 5.8485 | waste chp - back pressure - waste - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 11.2611 | waste chp - back pressure - waste - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 9.9638 | waste chp - back pressure - waste - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 5.9762 | waste chp - back pressure - waste - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 5.8273 | waste chp - back pressure - waste - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 5.6465 | waste chp - back pressure - waste - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 4.9553 | waste chp - back pressure - waste - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 4.9553 | waste chp - back pressure - waste - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 3.5517 | waste chp - back pressure - waste - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 6.9332 | waste chp - back pressure - waste - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 6.1463 | waste chp - back pressure - waste - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2015 | 3.86 | waste chp - back pressure - waste - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2020 | 3.7643 | waste chp - back pressure - waste - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2030 | 3.4985 | waste chp - back pressure - waste - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2050 | 3.0625 | waste chp - back pressure - waste - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2020 | 3.2008 | waste chp - back pressure - waste - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2050 | 2.2969 | waste chp - back pressure - waste - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2020 | 4.3279 | waste chp - back pressure - waste - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2050 | 3.8281 | waste chp - back pressure - waste - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2015 | 26.8821 | waste chp - back pressure - waste - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2020 | 26.8821 | waste chp - back pressure - waste - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2030 | 26.3078 | waste chp - back pressure - waste - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2050 | 25.4465 | waste chp - back pressure - waste - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2020 | 22.8731 | waste chp - back pressure - waste - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2050 | 19.1301 | waste chp - back pressure - waste - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2020 | 30.9867 | waste chp - back pressure - waste - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2050 | 31.7842 | waste chp - back pressure - waste - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0072 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 2 | waste chp - back pressure - waste - medium | regulation ability | cold start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 2 | waste chp - back pressure - waste - medium | regulation ability | cold start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 2 | waste chp - back pressure - waste - medium | regulation ability | cold start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 2 | waste chp - back pressure - waste - medium | regulation ability | cold start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 2 | waste chp - back pressure - waste - medium | regulation ability | cold start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 2 | waste chp - back pressure - waste - medium | regulation ability | cold start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 2 | waste chp - back pressure - waste - medium | regulation ability | cold start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 2 | waste chp - back pressure - waste - medium | regulation ability | cold start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2015 | 0.2 | waste chp - back pressure - waste - medium | regulation ability | minimum load (of full load) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2020 | 0.2 | waste chp - back pressure - waste - medium | regulation ability | minimum load (of full load) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2030 | 0.2 | waste chp - back pressure - waste - medium | regulation ability | minimum load (of full load) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2050 | 0.2 | waste chp - back pressure - waste - medium | regulation ability | minimum load (of full load) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2020 | 0.2 | waste chp - back pressure - waste - medium | regulation ability | minimum load (of full load) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2050 | 0.2 | waste chp - back pressure - waste - medium | regulation ability | minimum load (of full load) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2020 | 0.2 | waste chp - back pressure - waste - medium | regulation ability | minimum load (of full load) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2050 | 0.2 | waste chp - back pressure - waste - medium | regulation ability | minimum load (of full load) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2015 | 0.05 | waste chp - back pressure - waste - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2020 | 0.05 | waste chp - back pressure - waste - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2030 | 0.05 | waste chp - back pressure - waste - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2050 | 0.05 | waste chp - back pressure - waste - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2020 | 0.05 | waste chp - back pressure - waste - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2050 | 0.05 | waste chp - back pressure - waste - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2020 | 0.05 | waste chp - back pressure - waste - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2050 | 0.05 | waste chp - back pressure - waste - medium | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0171
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2015 | 0.1 | waste chp - back pressure - waste - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2020 | 0.1 | waste chp - back pressure - waste - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2030 | 0.1 | waste chp - back pressure - waste - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2050 | 0.1 | waste chp - back pressure - waste - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2020 | 0.1 | waste chp - back pressure - waste - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2050 | 0.1 | waste chp - back pressure - waste - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2020 | 0.1 | waste chp - back pressure - waste - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2050 | 0.1 | waste chp - back pressure - waste - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0072 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 0.5 | waste chp - back pressure - waste - medium | regulation ability | warm start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 0.5 | waste chp - back pressure - waste - medium | regulation ability | warm start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 0.5 | waste chp - back pressure - waste - medium | regulation ability | warm start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 0.5 | waste chp - back pressure - waste - medium | regulation ability | warm start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 0.5 | waste chp - back pressure - waste - medium | regulation ability | warm start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 0.5 | waste chp - back pressure - waste - medium | regulation ability | warm start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 0.5 | waste chp - back pressure - waste - medium | regulation ability | warm start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 0.5 | waste chp - back pressure - waste - medium | regulation ability | warm start-up time [hours] | ELH_0072 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.041506 | waste chp - back pressure - waste - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.041506 | waste chp - back pressure - waste - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.040149 | waste chp - back pressure - waste - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.037398 | waste chp - back pressure - waste - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.01 | waste chp - back pressure - waste - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.01 | waste chp - back pressure - waste - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.06 | waste chp - back pressure - waste - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.06 | waste chp - back pressure - waste - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | ctrl | 2015 | 0 | waste chp - back pressure - waste - medium | technology-specific data | combustion air humidification | ELH_0072 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | ctrl | 2020 | 0 | waste chp - back pressure - waste - medium | technology-specific data | combustion air humidification | ELH_0072 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | ctrl | 2030 | 0 | waste chp - back pressure - waste - medium | technology-specific data | combustion air humidification | ELH_0072 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | ctrl | 2050 | 0 | waste chp - back pressure - waste - medium | technology-specific data | combustion air humidification | ELH_0072 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | lower | 2020 | 0 | waste chp - back pressure - waste - medium | technology-specific data | combustion air humidification | ELH_0072 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | lower | 2050 | 0 | waste chp - back pressure - waste - medium | technology-specific data | combustion air humidification | ELH_0072 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | upper | 2020 | 1 | waste chp - back pressure - waste - medium | technology-specific data | combustion air humidification | ELH_0072 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | upper | 2050 | 1 | waste chp - back pressure - waste - medium | technology-specific data | combustion air humidification | ELH_0072 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 73691.7293 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 64865.7358 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 61888.2922 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 54657.3577 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 55189.044 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 40195.4887 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 75712.1375 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 68055.8539 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 27.1266 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 23.8834 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 22.7774 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 20.119 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 20.2998 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 14.7915 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 27.8604 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 25.0531 | waste chp - back pressure - waste - medium | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0072 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | ctrl | 2015 | 1 | waste chp - back pressure - waste - medium | technology-specific data | flue gas condensation | ELH_0072 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | ctrl | 2020 | 1 | waste chp - back pressure - waste - medium | technology-specific data | flue gas condensation | ELH_0072 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | ctrl | 2030 | 1 | waste chp - back pressure - waste - medium | technology-specific data | flue gas condensation | ELH_0072 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | ctrl | 2050 | 1 | waste chp - back pressure - waste - medium | technology-specific data | flue gas condensation | ELH_0072 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | lower | 2020 | 1 | waste chp - back pressure - waste - medium | technology-specific data | flue gas condensation | ELH_0072 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | lower | 2050 | 1 | waste chp - back pressure - waste - medium | technology-specific data | flue gas condensation | ELH_0072 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | upper | 2020 | 1 | waste chp - back pressure - waste - medium | technology-specific data | flue gas condensation | ELH_0072 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | upper | 2050 | 1 | waste chp - back pressure - waste - medium | technology-specific data | flue gas condensation | ELH_0072 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.79986 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.79986 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.79711 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.79418 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.76 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.73 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.85 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.88 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.78823 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.78823 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.78521 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.78187 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.74 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.71 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.84 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.86 | waste chp - back pressure - waste - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0072 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 27.16 | waste chp - back pressure - waste - medium | technology-specific data | incineration capacity [t_i/h] | ELH_0072 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 27.16 | waste chp - back pressure - waste - medium | technology-specific data | incineration capacity [t_i/h] | ELH_0072 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 27.16 | waste chp - back pressure - waste - medium | technology-specific data | incineration capacity [t_i/h] | ELH_0072 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 27.16 | waste chp - back pressure - waste - medium | technology-specific data | incineration capacity [t_i/h] | ELH_0072 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 27.16 | waste chp - back pressure - waste - medium | technology-specific data | incineration capacity [t_i/h] | ELH_0072 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 27.16 | waste chp - back pressure - waste - medium | technology-specific data | incineration capacity [t_i/h] | ELH_0072 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 27.16 | waste chp - back pressure - waste - medium | technology-specific data | incineration capacity [t_i/h] | ELH_0072 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 27.16 | waste chp - back pressure - waste - medium | technology-specific data | incineration capacity [t_i/h] | ELH_0072 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 2.2863 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 2.2331 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 2.1799 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.9779 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.8928 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.4356 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.6159 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.4564 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 840.0644 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 818.797 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 797.5295 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 723.0934 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 701.826 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 531.6864 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 967.6692 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 903.8668 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.393 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.3611 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.3398 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.2229 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.1484 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 0.87197 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.6163 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.51 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 0.89323 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.87197 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.82943 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.75499 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.74436 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.56359 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 1.0102 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 0.93577 | waste chp - back pressure - waste - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.4176 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.4176 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.4282 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.4495 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.6741 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.8664 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.2356 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 23.0433 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.11 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.11 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.12 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.1 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.1 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.14 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.14 | waste chp - back pressure - waste - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | ctrl | 2015 | 0 | waste chp - back pressure - waste - medium | technology-specific data | steam reheat | ELH_0072 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | ctrl | 2020 | 0 | waste chp - back pressure - waste - medium | technology-specific data | steam reheat | ELH_0072 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | ctrl | 2030 | 0 | waste chp - back pressure - waste - medium | technology-specific data | steam reheat | ELH_0072 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | ctrl | 2050 | 0 | waste chp - back pressure - waste - medium | technology-specific data | steam reheat | ELH_0072 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | lower | 2020 | 0 | waste chp - back pressure - waste - medium | technology-specific data | steam reheat | ELH_0072 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | lower | 2050 | 0 | waste chp - back pressure - waste - medium | technology-specific data | steam reheat | ELH_0072 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | upper | 2020 | 0 | waste chp - back pressure - waste - medium | technology-specific data | steam reheat | ELH_0072 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | upper | 2050 | 0 | waste chp - back pressure - waste - medium | technology-specific data | steam reheat | ELH_0072 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 6.2526 | waste chp - back pressure - waste - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 6.2526 | waste chp - back pressure - waste - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 6.2526 | waste chp - back pressure - waste - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 6.2633 | waste chp - back pressure - waste - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 5.3169 | waste chp - back pressure - waste - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 4.7107 | waste chp - back pressure - waste - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 7.2097 | waste chp - back pressure - waste - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 7.8264 | waste chp - back pressure - waste - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0072 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2015 | 0.029099 | waste chp - back pressure - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2020 | 0.029099 | waste chp - back pressure - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2030 | 0.029216 | waste chp - back pressure - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2050 | 0.029389 | waste chp - back pressure - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2020 | 0.021471 | waste chp - back pressure - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2050 | 0.017177 | waste chp - back pressure - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2020 | 0.032286 | waste chp - back pressure - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2050 | 0.032998 | waste chp - back pressure - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 0.29 | waste chp - back pressure - waste - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 0.29 | waste chp - back pressure - waste - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 0.29 | waste chp - back pressure - waste - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 0.3 | waste chp - back pressure - waste - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 0.26 | waste chp - back pressure - waste - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 0.26 | waste chp - back pressure - waste - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 0.31 | waste chp - back pressure - waste - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 0.33 | waste chp - back pressure - waste - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0014
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5 | waste chp - back pressure - waste - small | energy/technical data | construction time [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5 | waste chp - back pressure - waste - small | energy/technical data | construction time [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5 | waste chp - back pressure - waste - small | energy/technical data | construction time [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5 | waste chp - back pressure - waste - small | energy/technical data | construction time [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2 | waste chp - back pressure - waste - small | energy/technical data | construction time [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5 | waste chp - back pressure - waste - small | energy/technical data | construction time [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3 | waste chp - back pressure - waste - small | energy/technical data | construction time [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3 | waste chp - back pressure - waste - small | energy/technical data | construction time [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 1 | waste chp - back pressure - waste - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 1 | waste chp - back pressure - waste - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 1 | waste chp - back pressure - waste - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 1 | waste chp - back pressure - waste - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 1 | waste chp - back pressure - waste - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 1 | waste chp - back pressure - waste - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 1 | waste chp - back pressure - waste - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 1 | waste chp - back pressure - waste - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0073 | tk_etd | manual_category_map | PAR_0027
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.21592 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.21592 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.2203 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.22643 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.18 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.18 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.24 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.25 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0034
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.22729 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.22729 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.23189 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.23834 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2020 | 0.2 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2050 | 0.2 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2020 | 0.25 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2050 | 0.27 | waste chp - back pressure - waste - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0073 | tk_etd | manual_category_map | PAR_0036
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01 | waste chp - back pressure - waste - small | energy/technical data | forced outage [] | ELH_0073 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01 | waste chp - back pressure - waste - small | energy/technical data | forced outage [] | ELH_0073 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01 | waste chp - back pressure - waste - small | energy/technical data | forced outage [] | ELH_0073 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01 | waste chp - back pressure - waste - small | energy/technical data | forced outage [] | ELH_0073 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01 | waste chp - back pressure - waste - small | energy/technical data | forced outage [] | ELH_0073 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01 | waste chp - back pressure - waste - small | energy/technical data | forced outage [] | ELH_0073 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01 | waste chp - back pressure - waste - small | energy/technical data | forced outage [] | ELH_0073 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01 | waste chp - back pressure - waste - small | energy/technical data | forced outage [] | ELH_0073 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 7.96 | waste chp - back pressure - waste - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 7.96 | waste chp - back pressure - waste - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 8.12 | waste chp - back pressure - waste - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 8.34 | waste chp - back pressure - waste - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2020 | 7.25 | waste chp - back pressure - waste - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2050 | 7.25 | waste chp - back pressure - waste - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2020 | 8.62 | waste chp - back pressure - waste - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2050 | 9.19 | waste chp - back pressure - waste - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0071
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 3.5 | waste chp - back pressure - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0073 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 3.33 | waste chp - back pressure - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0073 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 3.01 | waste chp - back pressure - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0073 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 2.46 | waste chp - back pressure - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0073 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.83 | waste chp - back pressure - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0073 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.85 | waste chp - back pressure - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0073 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 3.83 | waste chp - back pressure - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0073 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 3.08 | waste chp - back pressure - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0073 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 2.51 | waste chp - back pressure - waste - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 2.51 | waste chp - back pressure - waste - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 2.46 | waste chp - back pressure - waste - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 2.4 | waste chp - back pressure - waste - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 2.14 | waste chp - back pressure - waste - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 1.8 | waste chp - back pressure - waste - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 2.89 | waste chp - back pressure - waste - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 3 | waste chp - back pressure - waste - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0073 | tk_etd | manual_category_map | PAR_0188
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | waste chp - back pressure - waste - small | energy/technical data | technical lifetime [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | waste chp - back pressure - waste - small | energy/technical data | technical lifetime [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | waste chp - back pressure - waste - small | energy/technical data | technical lifetime [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | waste chp - back pressure - waste - small | energy/technical data | technical lifetime [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | waste chp - back pressure - waste - small | energy/technical data | technical lifetime [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | waste chp - back pressure - waste - small | energy/technical data | technical lifetime [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | waste chp - back pressure - waste - small | energy/technical data | technical lifetime [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | waste chp - back pressure - waste - small | energy/technical data | technical lifetime [years] | ELH_0073 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3 | waste chp - back pressure - waste - small | environment | ch4 [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1 | waste chp - back pressure - waste - small | environment | ch4 [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1 | waste chp - back pressure - waste - small | environment | ch4 [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1 | waste chp - back pressure - waste - small | environment | ch4 [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0 | waste chp - back pressure - waste - small | environment | ch4 [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0 | waste chp - back pressure - waste - small | environment | ch4 [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1 | waste chp - back pressure - waste - small | environment | ch4 [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1 | waste chp - back pressure - waste - small | environment | ch4 [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2 | waste chp - back pressure - waste - small | environment | n2o [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1 | waste chp - back pressure - waste - small | environment | n2o [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1 | waste chp - back pressure - waste - small | environment | n2o [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1 | waste chp - back pressure - waste - small | environment | n2o [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1 | waste chp - back pressure - waste - small | environment | n2o [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0 | waste chp - back pressure - waste - small | environment | n2o [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3 | waste chp - back pressure - waste - small | environment | n2o [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste chp - back pressure - waste - small | environment | n2o [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80 | waste chp - back pressure - waste - small | environment | nox [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60 | waste chp - back pressure - waste - small | environment | nox [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40 | waste chp - back pressure - waste - small | environment | nox [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 20 | waste chp - back pressure - waste - small | environment | nox [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10 | waste chp - back pressure - waste - small | environment | nox [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10 | waste chp - back pressure - waste - small | environment | nox [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60 | waste chp - back pressure - waste - small | environment | nox [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60 | waste chp - back pressure - waste - small | environment | nox [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3 | waste chp - back pressure - waste - small | environment | particles [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3 | waste chp - back pressure - waste - small | environment | particles [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3 | waste chp - back pressure - waste - small | environment | particles [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3 | waste chp - back pressure - waste - small | environment | particles [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1 | waste chp - back pressure - waste - small | environment | particles [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1 | waste chp - back pressure - waste - small | environment | particles [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2 | waste chp - back pressure - waste - small | environment | particles [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste chp - back pressure - waste - small | environment | particles [g/gj_i] | ELH_0073 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792 | waste chp - back pressure - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0073 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792 | waste chp - back pressure - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0073 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792 | waste chp - back pressure - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0073 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792 | waste chp - back pressure - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0073 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962 | waste chp - back pressure - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0073 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481 | waste chp - back pressure - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0073 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896 | waste chp - back pressure - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0073 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896 | waste chp - back pressure - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0073 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2015 | 451933.4052 | waste chp - back pressure - waste - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0073 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2020 | 437046.1871 | waste chp - back pressure - waste - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0073 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2030 | 406208.3783 | waste chp - back pressure - waste - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0073 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2050 | 348786.2515 | waste chp - back pressure - waste - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0073 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2020 | 371117.0786 | waste chp - back pressure - waste - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0073 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2050 | 257336.1978 | waste chp - back pressure - waste - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0073 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2020 | 508292.1592 | waste chp - back pressure - waste - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0073 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2050 | 433856.0689 | waste chp - back pressure - waste - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0073 | tk_fin | manual_category_map | PAR_0042
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 11.3249 | waste chp - back pressure - waste - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 11.0484 | waste chp - back pressure - waste - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 10.5699 | waste chp - back pressure - waste - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 9.3258 | waste chp - back pressure - waste - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 9.3896 | waste chp - back pressure - waste - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 6.795 | waste chp - back pressure - waste - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 12.9838 | waste chp - back pressure - waste - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 11.5908 | waste chp - back pressure - waste - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0093
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 7.0502 | waste chp - back pressure - waste - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 6.8694 | waste chp - back pressure - waste - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 6.678 | waste chp - back pressure - waste - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 5.9017 | waste chp - back pressure - waste - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 5.8379 | waste chp - back pressure - waste - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 4.2322 | waste chp - back pressure - waste - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 8.1773 | waste chp - back pressure - waste - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 7.3054 | waste chp - back pressure - waste - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0104
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2015 | 4.2854 | waste chp - back pressure - waste - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2020 | 4.1791 | waste chp - back pressure - waste - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2030 | 3.8919 | waste chp - back pressure - waste - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2050 | 3.4241 | waste chp - back pressure - waste - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2020 | 3.5517 | waste chp - back pressure - waste - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2050 | 2.5734 | waste chp - back pressure - waste - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2020 | 4.8064 | waste chp - back pressure - waste - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2050 | 4.2854 | waste chp - back pressure - waste - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0115
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2015 | 27.5201 | waste chp - back pressure - waste - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2020 | 27.5201 | waste chp - back pressure - waste - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2030 | 26.9884 | waste chp - back pressure - waste - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2050 | 26.2653 | waste chp - back pressure - waste - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2020 | 23.4155 | waste chp - back pressure - waste - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2050 | 19.7468 | waste chp - back pressure - waste - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2020 | 31.6991 | waste chp - back pressure - waste - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2050 | 32.8157 | waste chp - back pressure - waste - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0073 | tk_fin | manual_category_map | PAR_0201
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 2 | waste chp - back pressure - waste - small | regulation ability | cold start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 2 | waste chp - back pressure - waste - small | regulation ability | cold start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 2 | waste chp - back pressure - waste - small | regulation ability | cold start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 2 | waste chp - back pressure - waste - small | regulation ability | cold start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 2 | waste chp - back pressure - waste - small | regulation ability | cold start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 2 | waste chp - back pressure - waste - small | regulation ability | cold start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 2 | waste chp - back pressure - waste - small | regulation ability | cold start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 2 | waste chp - back pressure - waste - small | regulation ability | cold start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2015 | 0.2 | waste chp - back pressure - waste - small | regulation ability | minimum load (of full load) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2020 | 0.2 | waste chp - back pressure - waste - small | regulation ability | minimum load (of full load) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2030 | 0.2 | waste chp - back pressure - waste - small | regulation ability | minimum load (of full load) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2050 | 0.2 | waste chp - back pressure - waste - small | regulation ability | minimum load (of full load) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2020 | 0.2 | waste chp - back pressure - waste - small | regulation ability | minimum load (of full load) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2050 | 0.2 | waste chp - back pressure - waste - small | regulation ability | minimum load (of full load) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2020 | 0.2 | waste chp - back pressure - waste - small | regulation ability | minimum load (of full load) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2050 | 0.2 | waste chp - back pressure - waste - small | regulation ability | minimum load (of full load) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2015 | 0.1 | waste chp - back pressure - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2020 | 0.1 | waste chp - back pressure - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2030 | 0.1 | waste chp - back pressure - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2050 | 0.1 | waste chp - back pressure - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2020 | 0.1 | waste chp - back pressure - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2050 | 0.1 | waste chp - back pressure - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2020 | 0.1 | waste chp - back pressure - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2050 | 0.1 | waste chp - back pressure - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0073 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 0.5 | waste chp - back pressure - waste - small | regulation ability | warm start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 0.5 | waste chp - back pressure - waste - small | regulation ability | warm start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 0.5 | waste chp - back pressure - waste - small | regulation ability | warm start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 0.5 | waste chp - back pressure - waste - small | regulation ability | warm start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 0.5 | waste chp - back pressure - waste - small | regulation ability | warm start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 0.5 | waste chp - back pressure - waste - small | regulation ability | warm start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 0.5 | waste chp - back pressure - waste - small | regulation ability | warm start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 0.5 | waste chp - back pressure - waste - small | regulation ability | warm start-up time [hours] | ELH_0073 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.041506 | waste chp - back pressure - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.041506 | waste chp - back pressure - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.040149 | waste chp - back pressure - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.038774 | waste chp - back pressure - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.01 | waste chp - back pressure - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.01 | waste chp - back pressure - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.06 | waste chp - back pressure - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.06 | waste chp - back pressure - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2015 | 0 | waste chp - back pressure - waste - small | technology-specific data | combustion air humidification | ELH_0073 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2020 | 0 | waste chp - back pressure - waste - small | technology-specific data | combustion air humidification | ELH_0073 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2030 | 0 | waste chp - back pressure - waste - small | technology-specific data | combustion air humidification | ELH_0073 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2050 | 0 | waste chp - back pressure - waste - small | technology-specific data | combustion air humidification | ELH_0073 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2020 | 0 | waste chp - back pressure - waste - small | technology-specific data | combustion air humidification | ELH_0073 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2050 | 0 | waste chp - back pressure - waste - small | technology-specific data | combustion air humidification | ELH_0073 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2020 | 1 | waste chp - back pressure - waste - small | technology-specific data | combustion air humidification | ELH_0073 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2050 | 1 | waste chp - back pressure - waste - small | technology-specific data | combustion air humidification | ELH_0073 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 102615.4672 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 99319.0118 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 94214.8228 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 83049.4092 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 84431.7938 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 61356.6058 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 115375.9398 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 103466.1654 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 37.8029 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 36.5481 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 34.6766 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 30.5613 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 31.0718 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 22.5754 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 42.4924 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 38.09 | waste chp - back pressure - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0073 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2015 | 1 | waste chp - back pressure - waste - small | technology-specific data | flue gas condensation | ELH_0073 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2020 | 1 | waste chp - back pressure - waste - small | technology-specific data | flue gas condensation | ELH_0073 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2030 | 1 | waste chp - back pressure - waste - small | technology-specific data | flue gas condensation | ELH_0073 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2050 | 1 | waste chp - back pressure - waste - small | technology-specific data | flue gas condensation | ELH_0073 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2020 | 1 | waste chp - back pressure - waste - small | technology-specific data | flue gas condensation | ELH_0073 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2050 | 1 | waste chp - back pressure - waste - small | technology-specific data | flue gas condensation | ELH_0073 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2020 | 1 | waste chp - back pressure - waste - small | technology-specific data | flue gas condensation | ELH_0073 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2050 | 1 | waste chp - back pressure - waste - small | technology-specific data | flue gas condensation | ELH_0073 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.80299 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.80299 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.80087 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.80493 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.77 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.74 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.86 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.88 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0076
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.79162 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.79162 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.78927 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.79302 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.75 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.72 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.85 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.86 | waste chp - back pressure - waste - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0073 | tk_tsd | manual_category_map | PAR_0077
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 11.88 | waste chp - back pressure - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0073 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 11.88 | waste chp - back pressure - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0073 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 11.88 | waste chp - back pressure - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0073 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 11.88 | waste chp - back pressure - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0073 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 11.88 | waste chp - back pressure - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0073 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 11.88 | waste chp - back pressure - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0073 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 11.88 | waste chp - back pressure - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0073 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 11.88 | waste chp - back pressure - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0073 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 3.2539 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 2.5096 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 2.4458 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 2.2224 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 2.1374 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.6163 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.9455 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.7648 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 946.4017 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 925.1343 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 903.8668 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 818.797 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 786.8958 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 595.4887 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 1084.6402 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 1020.8378 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 2.0204 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.5632 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.5525 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.4037 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.3292 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.0102 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.8609 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.7439 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 1.2335 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.9464 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.90387 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.8188 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.80816 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.61676 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 1.0953 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 1.0208 | waste chp - back pressure - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.4176 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.4176 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.4282 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.4389 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.6741 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.8664 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.2249 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 23.0433 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.11 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.11 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.12 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.1 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.1 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.14 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.14 | waste chp - back pressure - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2015 | 0 | waste chp - back pressure - waste - small | technology-specific data | steam reheat | ELH_0073 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2020 | 0 | waste chp - back pressure - waste - small | technology-specific data | steam reheat | ELH_0073 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2030 | 0 | waste chp - back pressure - waste - small | technology-specific data | steam reheat | ELH_0073 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2050 | 0 | waste chp - back pressure - waste - small | technology-specific data | steam reheat | ELH_0073 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | lower | 2020 | 0 | waste chp - back pressure - waste - small | technology-specific data | steam reheat | ELH_0073 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | lower | 2050 | 0 | waste chp - back pressure - waste - small | technology-specific data | steam reheat | ELH_0073 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | upper | 2020 | 0 | waste chp - back pressure - waste - small | technology-specific data | steam reheat | ELH_0073 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | upper | 2050 | 0 | waste chp - back pressure - waste - small | technology-specific data | steam reheat | ELH_0073 | tk_tsd | manual_category_map | PAR_0197
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 6.2526 | waste chp - back pressure - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 6.2526 | waste chp - back pressure - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 6.2526 | waste chp - back pressure - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 6.2633 | waste chp - back pressure - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 5.3169 | waste chp - back pressure - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 4.7107 | waste chp - back pressure - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 7.2097 | waste chp - back pressure - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 7.8264 | waste chp - back pressure - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0073 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.025848 | waste boiler - boiler - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.025848 | waste boiler - boiler - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.025501 | waste boiler - boiler - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.024842 | waste boiler - boiler - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | lower | 2020 | 0.019033 | waste boiler - boiler - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | lower | 2050 | 0.014903 | waste boiler - boiler - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | upper | 2020 | 0.027727 | waste boiler - boiler - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | upper | 2050 | 0.027608 | waste boiler - boiler - waste - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0005
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2 | waste boiler - boiler - waste - small | energy/technical data | construction time [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2 | waste boiler - boiler - waste - small | energy/technical data | construction time [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2 | waste boiler - boiler - waste - small | energy/technical data | construction time [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2 | waste boiler - boiler - waste - small | energy/technical data | construction time [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 1.5 | waste boiler - boiler - waste - small | energy/technical data | construction time [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5 | waste boiler - boiler - waste - small | energy/technical data | construction time [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 2.5 | waste boiler - boiler - waste - small | energy/technical data | construction time [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 2.5 | waste boiler - boiler - waste - small | energy/technical data | construction time [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0026
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01 | waste boiler - boiler - waste - small | energy/technical data | forced outage [] | ELH_0071 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01 | waste boiler - boiler - waste - small | energy/technical data | forced outage [] | ELH_0071 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01 | waste boiler - boiler - waste - small | energy/technical data | forced outage [] | ELH_0071 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01 | waste boiler - boiler - waste - small | energy/technical data | forced outage [] | ELH_0071 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01 | waste boiler - boiler - waste - small | energy/technical data | forced outage [] | ELH_0071 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01 | waste boiler - boiler - waste - small | energy/technical data | forced outage [] | ELH_0071 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01 | waste boiler - boiler - waste - small | energy/technical data | forced outage [] | ELH_0071 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01 | waste boiler - boiler - waste - small | energy/technical data | forced outage [] | ELH_0071 | tk_etd | manual_category_map | PAR_0065
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | ctrl | 2015 | 36.95 | waste boiler - boiler - waste - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0072
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | ctrl | 2020 | 36.95 | waste boiler - boiler - waste - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0072
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | ctrl | 2030 | 37.04 | waste boiler - boiler - waste - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0072
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | ctrl | 2050 | 37.21 | waste boiler - boiler - waste - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0072
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | lower | 2020 | 36.26 | waste boiler - boiler - waste - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0072
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | lower | 2050 | 36.26 | waste boiler - boiler - waste - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0072
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | upper | 2020 | 37.92 | waste boiler - boiler - waste - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0072
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | upper | 2050 | 38.08 | waste boiler - boiler - waste - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0072
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 1.0557 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0076
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 1.0557 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0076
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 1.0582 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0076
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 1.0633 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0076
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 1.03 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0076
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 1.03 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0076
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 1.09 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0076
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 1.09 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0076
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2015 | 1.0557 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0077
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2020 | 1.0557 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0077
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2030 | 1.0582 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0077
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2050 | 1.0633 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0077
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2020 | 1.03 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0077
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2050 | 1.03 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0077
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2020 | 1.09 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0077
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2050 | 1.09 | waste boiler - boiler - waste - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0071 | tk_etd | manual_category_map | PAR_0077
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 3 | waste boiler - boiler - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0071 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 2.85 | waste boiler - boiler - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0071 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 2.58 | waste boiler - boiler - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0071 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 2.11 | waste boiler - boiler - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0071 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.43 | waste boiler - boiler - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0071 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.58 | waste boiler - boiler - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0071 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 3.28 | waste boiler - boiler - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0071 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 2.64 | waste boiler - boiler - waste - small | energy/technical data | planned outage [weeks per year] | ELH_0071 | tk_etd | manual_category_map | PAR_0168
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | ctrl | 2015 | 0.54 | waste boiler - boiler - waste - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0189
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | ctrl | 2020 | 0.54 | waste boiler - boiler - waste - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0189
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | ctrl | 2030 | 0.54 | waste boiler - boiler - waste - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0189
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | ctrl | 2050 | 0.54 | waste boiler - boiler - waste - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0189
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | lower | 2020 | 0.46 | waste boiler - boiler - waste - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0189
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | lower | 2050 | 0.4 | waste boiler - boiler - waste - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0189
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | upper | 2020 | 0.62 | waste boiler - boiler - waste - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0189
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | upper | 2050 | 0.67 | waste boiler - boiler - waste - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0071 | tk_etd | manual_category_map | PAR_0189
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | waste boiler - boiler - waste - small | energy/technical data | technical lifetime [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | waste boiler - boiler - waste - small | energy/technical data | technical lifetime [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | waste boiler - boiler - waste - small | energy/technical data | technical lifetime [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | waste boiler - boiler - waste - small | energy/technical data | technical lifetime [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | waste boiler - boiler - waste - small | energy/technical data | technical lifetime [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | waste boiler - boiler - waste - small | energy/technical data | technical lifetime [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | waste boiler - boiler - waste - small | energy/technical data | technical lifetime [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | waste boiler - boiler - waste - small | energy/technical data | technical lifetime [years] | ELH_0071 | tk_etd | manual_category_map | PAR_0198
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3 | waste boiler - boiler - waste - small | environment | ch4 [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1 | waste boiler - boiler - waste - small | environment | ch4 [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1 | waste boiler - boiler - waste - small | environment | ch4 [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1 | waste boiler - boiler - waste - small | environment | ch4 [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0 | waste boiler - boiler - waste - small | environment | ch4 [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0 | waste boiler - boiler - waste - small | environment | ch4 [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1 | waste boiler - boiler - waste - small | environment | ch4 [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1 | waste boiler - boiler - waste - small | environment | ch4 [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0018
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2 | waste boiler - boiler - waste - small | environment | n2o [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1 | waste boiler - boiler - waste - small | environment | n2o [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1 | waste boiler - boiler - waste - small | environment | n2o [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1 | waste boiler - boiler - waste - small | environment | n2o [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1 | waste boiler - boiler - waste - small | environment | n2o [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0 | waste boiler - boiler - waste - small | environment | n2o [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3 | waste boiler - boiler - waste - small | environment | n2o [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste boiler - boiler - waste - small | environment | n2o [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0089
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80 | waste boiler - boiler - waste - small | environment | nox [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60 | waste boiler - boiler - waste - small | environment | nox [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40 | waste boiler - boiler - waste - small | environment | nox [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 20 | waste boiler - boiler - waste - small | environment | nox [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10 | waste boiler - boiler - waste - small | environment | nox [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10 | waste boiler - boiler - waste - small | environment | nox [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60 | waste boiler - boiler - waste - small | environment | nox [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60 | waste boiler - boiler - waste - small | environment | nox [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0152
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3 | waste boiler - boiler - waste - small | environment | particles [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3 | waste boiler - boiler - waste - small | environment | particles [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3 | waste boiler - boiler - waste - small | environment | particles [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3 | waste boiler - boiler - waste - small | environment | particles [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1 | waste boiler - boiler - waste - small | environment | particles [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1 | waste boiler - boiler - waste - small | environment | particles [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2 | waste boiler - boiler - waste - small | environment | particles [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1 | waste boiler - boiler - waste - small | environment | particles [g/gj_i] | ELH_0071 | tk_env | manual_category_map | PAR_0163
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792 | waste boiler - boiler - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0071 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792 | waste boiler - boiler - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0071 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792 | waste boiler - boiler - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0071 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792 | waste boiler - boiler - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0071 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962 | waste boiler - boiler - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0071 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481 | waste boiler - boiler - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0071 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896 | waste boiler - boiler - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0071 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896 | waste boiler - boiler - waste - small | environment | so2 (degree of desulphuring) [] | ELH_0071 | tk_env | manual_category_map | PAR_0181
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | ctrl | 2015 | 85814.1783 | waste boiler - boiler - waste - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0071 | tk_fin | manual_category_map | PAR_0043
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | ctrl | 2020 | 82943.072 | waste boiler - boiler - waste - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0071 | tk_fin | manual_category_map | PAR_0043
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | ctrl | 2030 | 78583.2439 | waste boiler - boiler - waste - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0071 | tk_fin | manual_category_map | PAR_0043
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | ctrl | 2050 | 68800.2149 | waste boiler - boiler - waste - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0071 | tk_fin | manual_category_map | PAR_0043
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | lower | 2020 | 71033.2976 | waste boiler - boiler - waste - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0071 | tk_fin | manual_category_map | PAR_0043
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | lower | 2050 | 52530.6123 | waste boiler - boiler - waste - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0071 | tk_fin | manual_category_map | PAR_0043
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | upper | 2020 | 97298.6037 | waste boiler - boiler - waste - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0071 | tk_fin | manual_category_map | PAR_0043
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | upper | 2050 | 88791.622 | waste boiler - boiler - waste - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0071 | tk_fin | manual_category_map | PAR_0043
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2015 | 1.8928 | waste boiler - boiler - waste - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0094
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2020 | 1.8503 | waste boiler - boiler - waste - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0094
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2030 | 1.8184 | waste boiler - boiler - waste - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0094
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2050 | 1.6376 | waste boiler - boiler - waste - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0094
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2020 | 1.6163 | waste boiler - boiler - waste - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0094
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2050 | 1.3079 | waste boiler - boiler - waste - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0094
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2020 | 2.2437 | waste boiler - boiler - waste - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0094
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2050 | 2.2437 | waste boiler - boiler - waste - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0094
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2015 | 1.0846 | waste boiler - boiler - waste - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0105
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2020 | 1.0634 | waste boiler - boiler - waste - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0105
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2030 | 1.0634 | waste boiler - boiler - waste - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0105
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2050 | 0.96767 | waste boiler - boiler - waste - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0105
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2020 | 0.92513 | waste boiler - boiler - waste - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0105
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2050 | 0.75499 | waste boiler - boiler - waste - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0105
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2020 | 1.3079 | waste boiler - boiler - waste - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0105
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2050 | 1.3079 | waste boiler - boiler - waste - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0105
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2015 | 0.80816 | waste boiler - boiler - waste - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0116
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2020 | 0.7869 | waste boiler - boiler - waste - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0116
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2030 | 0.74436 | waste boiler - boiler - waste - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0116
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2050 | 0.66992 | waste boiler - boiler - waste - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0116
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2020 | 0.69119 | waste boiler - boiler - waste - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0116
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2050 | 0.56359 | waste boiler - boiler - waste - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0116
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2020 | 0.92513 | waste boiler - boiler - waste - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0116
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2050 | 0.93577 | waste boiler - boiler - waste - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0116
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2015 | 7.6776 | waste boiler - boiler - waste - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0202
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2020 | 7.8477 | waste boiler - boiler - waste - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0202
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2030 | 8.6771 | waste boiler - boiler - waste - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0202
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2050 | 9.0068 | waste boiler - boiler - waste - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0202
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2020 | 6.7205 | waste boiler - boiler - waste - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0202
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2050 | 7.2947 | waste boiler - boiler - waste - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0202
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2020 | 8.9111 | waste boiler - boiler - waste - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0202
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2050 | 10.857 | waste boiler - boiler - waste - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0202
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2015 | 1.7333 | waste boiler - boiler - waste - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0206
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2020 | 1.8928 | waste boiler - boiler - waste - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0206
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2030 | 2.7435 | waste boiler - boiler - waste - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0206
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2050 | 3.0944 | waste boiler - boiler - waste - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0206
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2020 | 1.7758 | waste boiler - boiler - waste - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0206
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2050 | 2.9455 | waste boiler - boiler - waste - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0206
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2020 | 1.9353 | waste boiler - boiler - waste - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0206
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2050 | 3.2752 | waste boiler - boiler - waste - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0206
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2015 | 5.9443 | waste boiler - boiler - waste - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0208
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2020 | 5.9443 | waste boiler - boiler - waste - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0208
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2030 | 5.9336 | waste boiler - boiler - waste - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0208
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2050 | 5.9124 | waste boiler - boiler - waste - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0208
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2020 | 4.934 | waste boiler - boiler - waste - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0208
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2050 | 4.3492 | waste boiler - boiler - waste - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0208
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2020 | 6.9864 | waste boiler - boiler - waste - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0208
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2050 | 7.5818 | waste boiler - boiler - waste - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0071 | tk_fin | manual_category_map | PAR_0208
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | ctrl | 2015 | 12 | waste boiler - boiler - waste - small | regulation ability | cold start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | ctrl | 2020 | 12 | waste boiler - boiler - waste - small | regulation ability | cold start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | ctrl | 2030 | 12 | waste boiler - boiler - waste - small | regulation ability | cold start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | ctrl | 2050 | 12 | waste boiler - boiler - waste - small | regulation ability | cold start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | lower | 2020 | 12 | waste boiler - boiler - waste - small | regulation ability | cold start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | lower | 2050 | 12 | waste boiler - boiler - waste - small | regulation ability | cold start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | upper | 2020 | 12 | waste boiler - boiler - waste - small | regulation ability | cold start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | upper | 2050 | 12 | waste boiler - boiler - waste - small | regulation ability | cold start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0022
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2015 | 0.7 | waste boiler - boiler - waste - small | regulation ability | minimum load (of full load) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2020 | 0.7 | waste boiler - boiler - waste - small | regulation ability | minimum load (of full load) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2030 | 0.7 | waste boiler - boiler - waste - small | regulation ability | minimum load (of full load) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2050 | 0.7 | waste boiler - boiler - waste - small | regulation ability | minimum load (of full load) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | lower | 2020 | 0.7 | waste boiler - boiler - waste - small | regulation ability | minimum load (of full load) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | lower | 2050 | 0.7 | waste boiler - boiler - waste - small | regulation ability | minimum load (of full load) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | upper | 2020 | 0.7 | waste boiler - boiler - waste - small | regulation ability | minimum load (of full load) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | upper | 2050 | 0.7 | waste boiler - boiler - waste - small | regulation ability | minimum load (of full load) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0085
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2015 | 0.01 | waste boiler - boiler - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2020 | 0.01 | waste boiler - boiler - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2030 | 0.01 | waste boiler - boiler - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2050 | 0.01 | waste boiler - boiler - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | lower | 2020 | 0.01 | waste boiler - boiler - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | lower | 2050 | 0.01 | waste boiler - boiler - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | upper | 2020 | 0.01 | waste boiler - boiler - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | upper | 2050 | 0.01 | waste boiler - boiler - waste - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0071 | tk_reg | manual_category_map | PAR_0179
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | ctrl | 2015 | 8 | waste boiler - boiler - waste - small | regulation ability | warm start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | ctrl | 2020 | 8 | waste boiler - boiler - waste - small | regulation ability | warm start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | ctrl | 2030 | 8 | waste boiler - boiler - waste - small | regulation ability | warm start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | ctrl | 2050 | 8 | waste boiler - boiler - waste - small | regulation ability | warm start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | lower | 2020 | 8 | waste boiler - boiler - waste - small | regulation ability | warm start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | lower | 2050 | 8 | waste boiler - boiler - waste - small | regulation ability | warm start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | upper | 2020 | 8 | waste boiler - boiler - waste - small | regulation ability | warm start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | upper | 2050 | 8 | waste boiler - boiler - waste - small | regulation ability | warm start-up time [hours] | ELH_0071 | tk_reg | manual_category_map | PAR_0211
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.041506 | waste boiler - boiler - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0071 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.041506 | waste boiler - boiler - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0071 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.040149 | waste boiler - boiler - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0071 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.037398 | waste boiler - boiler - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0071 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.01 | waste boiler - boiler - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0071 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.01 | waste boiler - boiler - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0071 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.06 | waste boiler - boiler - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0071 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.06 | waste boiler - boiler - waste - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0071 | tk_tsd | manual_category_map | PAR_0003
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2015 | 0 | waste boiler - boiler - waste - small | technology-specific data | combustion air humidification | ELH_0071 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2020 | 0 | waste boiler - boiler - waste - small | technology-specific data | combustion air humidification | ELH_0071 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2030 | 0 | waste boiler - boiler - waste - small | technology-specific data | combustion air humidification | ELH_0071 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2050 | 0 | waste boiler - boiler - waste - small | technology-specific data | combustion air humidification | ELH_0071 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2020 | 0 | waste boiler - boiler - waste - small | technology-specific data | combustion air humidification | ELH_0071 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2050 | 0 | waste boiler - boiler - waste - small | technology-specific data | combustion air humidification | ELH_0071 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2020 | 1 | waste boiler - boiler - waste - small | technology-specific data | combustion air humidification | ELH_0071 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2050 | 1 | waste boiler - boiler - waste - small | technology-specific data | combustion air humidification | ELH_0071 | tk_tsd | manual_category_map | PAR_0025
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 90599.3555 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 87515.5747 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 83155.7465 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 73160.043 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 74967.7766 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 55933.4049 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 102721.8045 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 94427.4973 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0044
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 33.3367 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 32.2202 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 30.6039 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 26.9459 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 27.6158 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 20.5763 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 37.8242 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 34.751 | waste boiler - boiler - waste - small | technology-specific data | fixed o&m (*total) [eur/t_i/y] | ELH_0071 | tk_tsd | manual_category_map | PAR_0045
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2015 | 1 | waste boiler - boiler - waste - small | technology-specific data | flue gas condensation | ELH_0071 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2020 | 1 | waste boiler - boiler - waste - small | technology-specific data | flue gas condensation | ELH_0071 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2030 | 1 | waste boiler - boiler - waste - small | technology-specific data | flue gas condensation | ELH_0071 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2050 | 1 | waste boiler - boiler - waste - small | technology-specific data | flue gas condensation | ELH_0071 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2020 | 1 | waste boiler - boiler - waste - small | technology-specific data | flue gas condensation | ELH_0071 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2050 | 1 | waste boiler - boiler - waste - small | technology-specific data | flue gas condensation | ELH_0071 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2020 | 1 | waste boiler - boiler - waste - small | technology-specific data | flue gas condensation | ELH_0071 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2050 | 1 | waste boiler - boiler - waste - small | technology-specific data | flue gas condensation | ELH_0071 | tk_tsd | manual_category_map | PAR_0062
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 11.88 | waste boiler - boiler - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0071 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 11.88 | waste boiler - boiler - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0071 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 11.88 | waste boiler - boiler - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0071 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 11.88 | waste boiler - boiler - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0071 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 11.88 | waste boiler - boiler - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0071 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 11.88 | waste boiler - boiler - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0071 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 11.88 | waste boiler - boiler - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0071 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 11.88 | waste boiler - boiler - waste - small | technology-specific data | incineration capacity [t_i/h] | ELH_0071 | tk_tsd | manual_category_map | PAR_0081
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.9991 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.9566 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.9247 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.7439 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.7014 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.393 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.3607 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.382 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0095
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 733.7272 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 723.0934 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 701.826 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 638.0236 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 627.3899 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 510.4189 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 871.9656 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 882.5994 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (*total) [meur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0096
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.1484 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.1165 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.1272 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.0315 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 0.9783 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 0.79753 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.3824 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.393 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0106
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 0.8507 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.82943 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.7869 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.71246 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.72309 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.59549 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 0.9783 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 0.98894 | waste boiler - boiler - waste - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0117
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 23.8834 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 24.3938 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 27.0416 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 28.2006 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 21.427 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 23.3729 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 27.2117 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 33.1347 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0159
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.13824 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.13824 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.14887 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.14887 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.1276 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.1276 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.18077 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.18077 | waste boiler - boiler - waste - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0160
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 8.1029 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 8.2837 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 9.1769 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 9.5704 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 7.2735 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 7.9328 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 9.2407 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 11.2505 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0203
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 5.3807 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (electricity cost) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0207
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 5.9017 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (electricity cost) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0207
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 8.5389 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (electricity cost) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0207
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 9.6767 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (electricity cost) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0207
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 5.6784 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (electricity cost) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0207
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 9.4321 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (electricity cost) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0207
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 5.9017 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (electricity cost) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0207
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 10.0063 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (electricity cost) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0207
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.4921 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (other o&m) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0209
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.4921 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (other o&m) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0209
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.5027 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (other o&m) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0209
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.524 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (other o&m) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0209
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.7485 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (other o&m) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0209
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.9408 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (other o&m) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0209
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.31 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (other o&m) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0209
ELH | 08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 23.1284 | waste boiler - boiler - waste - small | technology-specific data | variable o&m (other o&m) [eur/t_i] | ELH_0071 | tk_tsd | manual_category_map | PAR_0209
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.029624 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.02941 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.029426 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.02935 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.021813 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017993 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.032721 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.034321 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.37 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.37 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.38 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.37 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.34 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.35 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.5 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.51 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 4.5 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 4 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5.5 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5.5 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0015 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.28855 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.28915 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.29019 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.28513 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.24 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.26 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.39 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.4 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.30373 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.30437 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.30547 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.30014 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.27 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.29 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.41 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.42 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0015 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0015 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0015 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0015 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0015 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0015 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0015 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0015 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0015 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 182.24 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 182.62 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 183.28 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 180.08 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 166.32 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 174.4 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 242.89 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 251.01 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0015 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0015 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0015 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0015 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0015 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0015 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0015 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0015 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.08 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.08 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.08 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.08 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.07 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.06 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.09 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.1 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0015 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp, 40/80 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0015 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0015 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0015 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0015 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0015 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0015 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2020 | 0.94925 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0015 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2050 | 0.9797 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0015 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2020 | 0.98985 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0015 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2050 | 0.98985 | biomass chp, 40/80 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0015 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 103147.1536 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0015 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 101020.4082 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0015 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 94640.1719 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0015 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 89323.3083 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0015 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 85069.8174 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0015 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 68055.854 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0015 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 118034.3717 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0015 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 116970.999 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0015 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.5942 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.4985 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.3177 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.1263 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.9668 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.467 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.1897 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.2854 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.3288 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.265 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.148 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.0417 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.8928 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.5738 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.7435 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 2.7967 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.2654 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.2335 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.1697 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.074 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.074 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.89323 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.4568 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.4887 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.6682 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.6682 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.6469 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.732 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.3071 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 2.9562 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 5.2424 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 5.7103 | biomass chp, 40/80 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0015 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 12 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 12 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 12 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 12 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 12 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 12 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 12 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 12 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.45 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0015 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2015 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2030 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2050 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2050 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2050 | 2 | biomass chp, 40/80 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0015 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.019432 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.018691 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.018689 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.018699 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.28 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.28 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0015 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0015 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0015 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0015 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0015 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0015 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0015 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0015 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 31369.4952 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0015 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 30625.1343 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0015 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 29030.0752 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0015 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 26690.6552 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0015 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 25839.957 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0015 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 20310.4189 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0015 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 36048.3351 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0015 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 34984.9624 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0015 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0015 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0015 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0015 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0015 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0015 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0015 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0015 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0015 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.010634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0015 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.010634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0015 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.010634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0015 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.010634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0015 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.010634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0015 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.010634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0015 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.010634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0015 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.010634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0015 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.82914 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.83067 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.8296 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.83481 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.47 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.46 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.87 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.85 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.81395 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.81545 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.81433 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.8198 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.44 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.43 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.85 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.83 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0015 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0953 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.0634 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.0102 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.93577 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.90387 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.74436 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.276 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.2867 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.70183 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.69119 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.65929 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.61676 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.57422 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.46788 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.82943 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.84006 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.38281 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.37218 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.36155 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.31901 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.32965 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.26584 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.44662 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.44662 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.22 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.22 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.22 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.22 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.22 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.22 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0015 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0015 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0015 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0015 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0015 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0015 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0015 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0015 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.4143 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.4249 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.4249 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.4249 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.0102 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.8826 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.5951 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.712 | biomass chp, 40/80 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0015 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.029781 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.029563 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.029578 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.029502 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.022017 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.018156 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.032889 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.034488 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.35 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.35 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.35 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.34 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.32 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.33 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.47 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.49 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 4.5 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 4 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5.5 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5.5 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | construction time [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0018 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.26842 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.26892 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.26991 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.26517 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.23 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.24 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.37 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.38 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.28255 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.28307 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.28411 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.27913 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.25 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.27 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.39 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.4 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0018 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0018 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0018 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0018 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0018 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0018 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0018 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0018 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | forced outage [] | ELH_0018 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 169.53 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 169.84 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 170.47 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 167.48 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 153.68 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 162.19 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 230.21 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 238.75 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0018 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0018 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0018 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0018 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0018 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0018 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0018 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0018 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.09 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.09 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.09 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.09 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.08 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.07 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.1 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.11 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0018 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp, 50/100 degree - back pressure - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0018 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | ch4 [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | n2o [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | nox [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | particles [g/gj_i] | ELH_0018 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0018 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0018 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0018 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0018 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2020 | 0.94925 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0018 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2050 | 0.9797 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0018 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2020 | 0.98985 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0018 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2050 | 0.98985 | biomass chp, 50/100 degree - back pressure - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0018 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 111654.1354 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0018 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 108464.0172 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0018 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 102083.7809 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0018 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 95703.5446 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0018 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 91450.0537 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0018 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 73372.7175 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0018 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 127604.7262 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0018 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 125477.9807 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0018 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.86 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.7537 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.5623 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.3603 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.1901 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.6478 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.5087 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.6044 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.4989 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.4351 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.3075 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.2012 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 2.0417 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.6908 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.9455 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 3.0093 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.3611 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.3292 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.2548 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.1591 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.1591 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.95704 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.5632 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.5951 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.8915 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.8915 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.8702 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.966 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.5517 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 3.1795 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 5.5189 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 6.0187 | biomass chp, 50/100 degree - back pressure - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0018 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 12 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 12 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 12 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 12 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 12 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 12 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 12 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 12 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0018 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2015 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2030 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2050 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2050 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2050 | 2 | biomass chp, 50/100 degree - back pressure - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0018 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.046395 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.044624 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.04462 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.044641 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.28 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.28 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0018 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0018 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0018 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0018 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0018 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0018 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0018 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | combustion air humidification | ELH_0018 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 31369.4952 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0018 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 30625.1343 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0018 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 29030.0752 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0018 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 26690.6552 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0018 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 25839.957 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0018 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 20310.4189 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0018 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 36048.3351 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0018 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 34984.9624 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0018 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0018 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0018 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0018 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0018 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0018 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0018 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0018 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | flue gas condensation | ELH_0018 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.010634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0018 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.010634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0018 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.010634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0018 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.010634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0018 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.010634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0018 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.010634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0018 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.010634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0018 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.010634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0018 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.82282 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.82553 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.82451 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.82939 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.48 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.48 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.86 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.85 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.80869 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.81138 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.8103 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.81543 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.46 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.45 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.84 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.83 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0018 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0953 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.0634 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.0102 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.93577 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.90387 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.74436 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.276 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.2867 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.70183 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.69119 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.65929 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.61676 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.57422 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.46788 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.82943 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.84006 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.38281 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.37218 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.36155 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.31901 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.32965 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.26584 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.44662 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.44662 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.19 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.19 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.19 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.19 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.19 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.19 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0018 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0018 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0018 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0018 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0018 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0018 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0018 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | steam reheat | ELH_0018 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.3824 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.3824 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.3824 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.3824 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.0102 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.8826 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.5632 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.6801 | biomass chp, 50/100 degree - back pressure - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0018 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.029611 | biomass chp - back pressure - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.029611 | biomass chp - back pressure - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.029627 | biomass chp - back pressure - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.029548 | biomass chp - back pressure - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.021853 | biomass chp - back pressure - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017985 | biomass chp - back pressure - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.032707 | biomass chp - back pressure - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.034305 | biomass chp - back pressure - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.37 | biomass chp - back pressure - wood chips - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.37 | biomass chp - back pressure - wood chips - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.37 | biomass chp - back pressure - wood chips - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.36 | biomass chp - back pressure - wood chips - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.34 | biomass chp - back pressure - wood chips - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.35 | biomass chp - back pressure - wood chips - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.49 | biomass chp - back pressure - wood chips - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.5 | biomass chp - back pressure - wood chips - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5 | biomass chp - back pressure - wood chips - medium | energy/technical data | construction time [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5 | biomass chp - back pressure - wood chips - medium | energy/technical data | construction time [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5 | biomass chp - back pressure - wood chips - medium | energy/technical data | construction time [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5 | biomass chp - back pressure - wood chips - medium | energy/technical data | construction time [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2 | biomass chp - back pressure - wood chips - medium | energy/technical data | construction time [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5 | biomass chp - back pressure - wood chips - medium | energy/technical data | construction time [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3 | biomass chp - back pressure - wood chips - medium | energy/technical data | construction time [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3 | biomass chp - back pressure - wood chips - medium | energy/technical data | construction time [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood chips - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp - back pressure - wood chips - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp - back pressure - wood chips - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp - back pressure - wood chips - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp - back pressure - wood chips - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0008 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.28227 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.28227 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.28335 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.27821 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.24 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.25 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.38 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.39 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.29713 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.29713 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.29826 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.29285 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.27 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.28 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.4 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.41 | biomass chp - back pressure - wood chips - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0008 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp - back pressure - wood chips - medium | energy/technical data | forced outage [] | ELH_0008 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp - back pressure - wood chips - medium | energy/technical data | forced outage [] | ELH_0008 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp - back pressure - wood chips - medium | energy/technical data | forced outage [] | ELH_0008 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp - back pressure - wood chips - medium | energy/technical data | forced outage [] | ELH_0008 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp - back pressure - wood chips - medium | energy/technical data | forced outage [] | ELH_0008 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp - back pressure - wood chips - medium | energy/technical data | forced outage [] | ELH_0008 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp - back pressure - wood chips - medium | energy/technical data | forced outage [] | ELH_0008 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp - back pressure - wood chips - medium | energy/technical data | forced outage [] | ELH_0008 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 23.77 | biomass chp - back pressure - wood chips - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 23.77 | biomass chp - back pressure - wood chips - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 23.86 | biomass chp - back pressure - wood chips - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 23.43 | biomass chp - back pressure - wood chips - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 22.17 | biomass chp - back pressure - wood chips - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 22.74 | biomass chp - back pressure - wood chips - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 31.78 | biomass chp - back pressure - wood chips - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 32.73 | biomass chp - back pressure - wood chips - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp - back pressure - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0008 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp - back pressure - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0008 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp - back pressure - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0008 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp - back pressure - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0008 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp - back pressure - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0008 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp - back pressure - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0008 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp - back pressure - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0008 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp - back pressure - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0008 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.21 | biomass chp - back pressure - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.21 | biomass chp - back pressure - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.21 | biomass chp - back pressure - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.21 | biomass chp - back pressure - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.18 | biomass chp - back pressure - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.16 | biomass chp - back pressure - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.24 | biomass chp - back pressure - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.27 | biomass chp - back pressure - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0008 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp - back pressure - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp - back pressure - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp - back pressure - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp - back pressure - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp - back pressure - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp - back pressure - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp - back pressure - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp - back pressure - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0008 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3 | biomass chp - back pressure - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2 | biomass chp - back pressure - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2 | biomass chp - back pressure - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1 | biomass chp - back pressure - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0 | biomass chp - back pressure - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3 | biomass chp - back pressure - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3 | biomass chp - back pressure - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 1.2 | biomass chp - back pressure - wood chips - medium | environment | n2o [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - medium | environment | n2o [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - medium | environment | n2o [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - medium | environment | n2o [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1 | biomass chp - back pressure - wood chips - medium | environment | n2o [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0 | biomass chp - back pressure - wood chips - medium | environment | n2o [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3 | biomass chp - back pressure - wood chips - medium | environment | n2o [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1 | biomass chp - back pressure - wood chips - medium | environment | n2o [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 90 | biomass chp - back pressure - wood chips - medium | environment | nox [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 60 | biomass chp - back pressure - wood chips - medium | environment | nox [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 40 | biomass chp - back pressure - wood chips - medium | environment | nox [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 20 | biomass chp - back pressure - wood chips - medium | environment | nox [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 40 | biomass chp - back pressure - wood chips - medium | environment | nox [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 20 | biomass chp - back pressure - wood chips - medium | environment | nox [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 60 | biomass chp - back pressure - wood chips - medium | environment | nox [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 40 | biomass chp - back pressure - wood chips - medium | environment | nox [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 2 | biomass chp - back pressure - wood chips - medium | environment | particles [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3 | biomass chp - back pressure - wood chips - medium | environment | particles [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3 | biomass chp - back pressure - wood chips - medium | environment | particles [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3 | biomass chp - back pressure - wood chips - medium | environment | particles [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1 | biomass chp - back pressure - wood chips - medium | environment | particles [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1 | biomass chp - back pressure - wood chips - medium | environment | particles [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2 | biomass chp - back pressure - wood chips - medium | environment | particles [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1 | biomass chp - back pressure - wood chips - medium | environment | particles [g/gj_i] | ELH_0008 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797 | biomass chp - back pressure - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0008 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797 | biomass chp - back pressure - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0008 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797 | biomass chp - back pressure - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0008 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797 | biomass chp - back pressure - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0008 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2020 | 0.94925 | biomass chp - back pressure - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0008 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2050 | 0.9797 | biomass chp - back pressure - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0008 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2020 | 0.98985 | biomass chp - back pressure - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0008 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2050 | 0.98985 | biomass chp - back pressure - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0008 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 163759.3986 | biomass chp - back pressure - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0008 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 158442.535 | biomass chp - back pressure - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0008 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 148872.1805 | biomass chp - back pressure - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0008 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 137175.0806 | biomass chp - back pressure - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0008 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 133984.9625 | biomass chp - back pressure - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0008 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 103147.1536 | biomass chp - back pressure - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0008 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 183963.4802 | biomass chp - back pressure - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0008 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 177583.2439 | biomass chp - back pressure - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0008 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.86 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.7643 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.5729 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.4028 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.1582 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.6159 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.4449 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.6576 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.584 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.5202 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.3926 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.3075 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 2.0736 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.7227 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.9774 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 3.1476 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.276 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.2441 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.1803 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.0846 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.0846 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.90387 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.4675 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.4994 | biomass chp - back pressure - wood chips - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.7745 | biomass chp - back pressure - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.7745 | biomass chp - back pressure - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.7533 | biomass chp - back pressure - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.8383 | biomass chp - back pressure - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.3815 | biomass chp - back pressure - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 3.0306 | biomass chp - back pressure - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 5.3807 | biomass chp - back pressure - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 5.8592 | biomass chp - back pressure - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0008 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8 | biomass chp - back pressure - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8 | biomass chp - back pressure - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8 | biomass chp - back pressure - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8 | biomass chp - back pressure - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8 | biomass chp - back pressure - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8 | biomass chp - back pressure - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8 | biomass chp - back pressure - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8 | biomass chp - back pressure - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.2 | biomass chp - back pressure - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.2 | biomass chp - back pressure - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.2 | biomass chp - back pressure - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.2 | biomass chp - back pressure - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.2 | biomass chp - back pressure - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.2 | biomass chp - back pressure - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.2 | biomass chp - back pressure - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.2 | biomass chp - back pressure - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp - back pressure - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp - back pressure - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp - back pressure - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp - back pressure - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp - back pressure - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp - back pressure - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp - back pressure - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp - back pressure - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0008 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2015 | 2 | biomass chp - back pressure - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2020 | 2 | biomass chp - back pressure - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2030 | 2 | biomass chp - back pressure - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2050 | 2 | biomass chp - back pressure - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2020 | 2 | biomass chp - back pressure - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2050 | 2 | biomass chp - back pressure - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2020 | 2 | biomass chp - back pressure - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2050 | 2 | biomass chp - back pressure - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0008 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.019432 | biomass chp - back pressure - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.019432 | biomass chp - back pressure - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.01943 | biomass chp - back pressure - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.01944 | biomass chp - back pressure - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp - back pressure - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp - back pressure - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.26 | biomass chp - back pressure - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.28 | biomass chp - back pressure - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | combustion air humidification | ELH_0008 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | combustion air humidification | ELH_0008 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | combustion air humidification | ELH_0008 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | combustion air humidification | ELH_0008 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | combustion air humidification | ELH_0008 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | combustion air humidification | ELH_0008 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | combustion air humidification | ELH_0008 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | combustion air humidification | ELH_0008 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 48702.4705 | biomass chp - back pressure - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0008 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 47213.7487 | biomass chp - back pressure - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0008 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 44448.9796 | biomass chp - back pressure - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0008 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 40195.4887 | biomass chp - back pressure - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0008 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 39663.8024 | biomass chp - back pressure - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0008 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 30093.4479 | biomass chp - back pressure - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0008 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 54763.695 | biomass chp - back pressure - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0008 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 51892.5886 | biomass chp - back pressure - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0008 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | flue gas condensation | ELH_0008 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | flue gas condensation | ELH_0008 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | flue gas condensation | ELH_0008 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | flue gas condensation | ELH_0008 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | flue gas condensation | ELH_0008 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | flue gas condensation | ELH_0008 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | flue gas condensation | ELH_0008 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | flue gas condensation | ELH_0008 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.010634 | biomass chp - back pressure - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0008 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.010634 | biomass chp - back pressure - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0008 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.010634 | biomass chp - back pressure - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0008 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.010634 | biomass chp - back pressure - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0008 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.010634 | biomass chp - back pressure - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0008 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.010634 | biomass chp - back pressure - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0008 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.021267 | biomass chp - back pressure - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0008 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.021267 | biomass chp - back pressure - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0008 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.82723 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.82723 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.82611 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.83147 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.49 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.46 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.86 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.85 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.81237 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.81237 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.81119 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.81683 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.46 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.43 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.84 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.83 | biomass chp - back pressure - wood chips - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0008 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.1484 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.1165 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.0634 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.99957 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.93577 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.76563 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.3186 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.3611 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.76563 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.75499 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.71246 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.68056 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.61676 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.49979 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.8826 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.92513 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.38281 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.37218 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.35091 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.31901 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.31901 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.26584 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.43598 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.43598 | biomass chp - back pressure - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.22 | biomass chp - back pressure - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.22 | biomass chp - back pressure - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.22 | biomass chp - back pressure - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.22 | biomass chp - back pressure - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.22 | biomass chp - back pressure - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.22 | biomass chp - back pressure - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | steam reheat | ELH_0008 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | steam reheat | ELH_0008 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | steam reheat | ELH_0008 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | steam reheat | ELH_0008 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | steam reheat | ELH_0008 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp - back pressure - wood chips - medium | technology-specific data | steam reheat | ELH_0008 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | steam reheat | ELH_0008 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp - back pressure - wood chips - medium | technology-specific data | steam reheat | ELH_0008 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.4143 | biomass chp - back pressure - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.4143 | biomass chp - back pressure - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.4143 | biomass chp - back pressure - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.4143 | biomass chp - back pressure - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.0102 | biomass chp - back pressure - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.8826 | biomass chp - back pressure - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.5951 | biomass chp - back pressure - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.712 | biomass chp - back pressure - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0008 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.02734 | biomass chp - back pressure - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.02734 | biomass chp - back pressure - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.02735 | biomass chp - back pressure - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.027299 | biomass chp - back pressure - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.020804 | biomass chp - back pressure - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.016612 | biomass chp - back pressure - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.029894 | biomass chp - back pressure - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.029899 | biomass chp - back pressure - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.14 | biomass chp - back pressure - wood chips - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0014
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | construction time [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | construction time [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | construction time [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | construction time [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5 | biomass chp - back pressure - wood chips - small | energy/technical data | construction time [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5 | biomass chp - back pressure - wood chips - small | energy/technical data | construction time [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5 | biomass chp - back pressure - wood chips - small | energy/technical data | construction time [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5 | biomass chp - back pressure - wood chips - small | energy/technical data | construction time [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp - back pressure - wood chips - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0009 | tk_etd | manual_category_map | PAR_0027
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.13932 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.13932 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.13987 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.13713 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.12 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.12 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.14665 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.14665 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.14723 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.14435 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.14 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.13 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.15 | biomass chp - back pressure - wood chips - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0009 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp - back pressure - wood chips - small | energy/technical data | forced outage [] | ELH_0009 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp - back pressure - wood chips - small | energy/technical data | forced outage [] | ELH_0009 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp - back pressure - wood chips - small | energy/technical data | forced outage [] | ELH_0009 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp - back pressure - wood chips - small | energy/technical data | forced outage [] | ELH_0009 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp - back pressure - wood chips - small | energy/technical data | forced outage [] | ELH_0009 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp - back pressure - wood chips - small | energy/technical data | forced outage [] | ELH_0009 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp - back pressure - wood chips - small | energy/technical data | forced outage [] | ELH_0009 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp - back pressure - wood chips - small | energy/technical data | forced outage [] | ELH_0009 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 2.93 | biomass chp - back pressure - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 2.93 | biomass chp - back pressure - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 2.94 | biomass chp - back pressure - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 2.89 | biomass chp - back pressure - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 2.85 | biomass chp - back pressure - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 2.79 | biomass chp - back pressure - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 2.97 | biomass chp - back pressure - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 2.98 | biomass chp - back pressure - wood chips - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp - back pressure - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0009 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp - back pressure - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0009 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp - back pressure - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0009 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp - back pressure - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0009 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp - back pressure - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0009 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp - back pressure - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0009 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp - back pressure - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0009 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp - back pressure - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0009 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.68 | biomass chp - back pressure - wood chips - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.68 | biomass chp - back pressure - wood chips - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.68 | biomass chp - back pressure - wood chips - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.69 | biomass chp - back pressure - wood chips - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.58 | biomass chp - back pressure - wood chips - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.52 | biomass chp - back pressure - wood chips - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.78 | biomass chp - back pressure - wood chips - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.87 | biomass chp - back pressure - wood chips - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0009 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp - back pressure - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp - back pressure - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp - back pressure - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp - back pressure - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp - back pressure - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp - back pressure - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp - back pressure - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp - back pressure - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0009 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 20 | biomass chp - back pressure - wood chips - small | environment | ch4 [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 10 | biomass chp - back pressure - wood chips - small | environment | ch4 [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 8 | biomass chp - back pressure - wood chips - small | environment | ch4 [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 4 | biomass chp - back pressure - wood chips - small | environment | ch4 [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 4 | biomass chp - back pressure - wood chips - small | environment | ch4 [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 2 | biomass chp - back pressure - wood chips - small | environment | ch4 [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 16 | biomass chp - back pressure - wood chips - small | environment | ch4 [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 16 | biomass chp - back pressure - wood chips - small | environment | ch4 [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2 | biomass chp - back pressure - wood chips - small | environment | n2o [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - small | environment | n2o [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - small | environment | n2o [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - small | environment | n2o [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1 | biomass chp - back pressure - wood chips - small | environment | n2o [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp - back pressure - wood chips - small | environment | n2o [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3 | biomass chp - back pressure - wood chips - small | environment | n2o [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp - back pressure - wood chips - small | environment | n2o [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 90 | biomass chp - back pressure - wood chips - small | environment | nox [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 60 | biomass chp - back pressure - wood chips - small | environment | nox [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 40 | biomass chp - back pressure - wood chips - small | environment | nox [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 30 | biomass chp - back pressure - wood chips - small | environment | nox [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 40 | biomass chp - back pressure - wood chips - small | environment | nox [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 20 | biomass chp - back pressure - wood chips - small | environment | nox [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 80 | biomass chp - back pressure - wood chips - small | environment | nox [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 40 | biomass chp - back pressure - wood chips - small | environment | nox [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2 | biomass chp - back pressure - wood chips - small | environment | particles [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3 | biomass chp - back pressure - wood chips - small | environment | particles [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3 | biomass chp - back pressure - wood chips - small | environment | particles [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3 | biomass chp - back pressure - wood chips - small | environment | particles [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1 | biomass chp - back pressure - wood chips - small | environment | particles [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1 | biomass chp - back pressure - wood chips - small | environment | particles [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2 | biomass chp - back pressure - wood chips - small | environment | particles [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp - back pressure - wood chips - small | environment | particles [g/gj_i] | ELH_0009 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9797 | biomass chp - back pressure - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0009 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9797 | biomass chp - back pressure - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0009 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9797 | biomass chp - back pressure - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0009 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.9797 | biomass chp - back pressure - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0009 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.94925 | biomass chp - back pressure - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0009 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9797 | biomass chp - back pressure - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0009 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.98985 | biomass chp - back pressure - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0009 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.98985 | biomass chp - back pressure - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0009 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 303061.2246 | biomass chp - back pressure - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0009 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 298807.7338 | biomass chp - back pressure - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0009 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 290300.752 | biomass chp - back pressure - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0009 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 287110.6339 | biomass chp - back pressure - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0009 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 256272.825 | biomass chp - back pressure - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0009 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 217991.4072 | biomass chp - back pressure - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0009 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 346659.5061 | biomass chp - back pressure - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0009 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 368990.3331 | biomass chp - back pressure - wood chips - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0009 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2015 | 6.8907 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2020 | 6.7205 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2030 | 6.3696 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2050 | 6.1676 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2020 | 5.8592 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2050 | 4.8702 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2020 | 7.9221 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2050 | 8.4113 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 4.2748 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 4.1684 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 3.9557 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 3.9345 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 3.6367 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 3.02 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 4.9234 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 5.3275 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.6053 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.5415 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.4139 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.2224 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 2.2224 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.8396 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.9987 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 3.0731 | biomass chp - back pressure - wood chips - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 9.8468 | biomass chp - back pressure - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 9.8468 | biomass chp - back pressure - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 9.8043 | biomass chp - back pressure - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 10.0063 | biomass chp - back pressure - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 6.8588 | biomass chp - back pressure - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 6.1463 | biomass chp - back pressure - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 11.0697 | biomass chp - back pressure - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 12.0693 | biomass chp - back pressure - wood chips - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0009 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5 | biomass chp - back pressure - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5 | biomass chp - back pressure - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5 | biomass chp - back pressure - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5 | biomass chp - back pressure - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5 | biomass chp - back pressure - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5 | biomass chp - back pressure - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5 | biomass chp - back pressure - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5 | biomass chp - back pressure - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2015 | 0.2 | biomass chp - back pressure - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2020 | 0.2 | biomass chp - back pressure - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2030 | 0.2 | biomass chp - back pressure - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2050 | 0.2 | biomass chp - back pressure - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2020 | 0.2 | biomass chp - back pressure - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2050 | 0.2 | biomass chp - back pressure - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2020 | 0.2 | biomass chp - back pressure - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2050 | 0.2 | biomass chp - back pressure - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.1 | biomass chp - back pressure - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.1 | biomass chp - back pressure - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.1 | biomass chp - back pressure - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.1 | biomass chp - back pressure - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.1 | biomass chp - back pressure - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.1 | biomass chp - back pressure - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.1 | biomass chp - back pressure - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.1 | biomass chp - back pressure - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0009 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 0.25 | biomass chp - back pressure - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 0.25 | biomass chp - back pressure - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 0.25 | biomass chp - back pressure - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 0.25 | biomass chp - back pressure - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 0.25 | biomass chp - back pressure - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 0.25 | biomass chp - back pressure - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 0.25 | biomass chp - back pressure - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 0.25 | biomass chp - back pressure - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0009 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.019432 | biomass chp - back pressure - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.019432 | biomass chp - back pressure - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.01943 | biomass chp - back pressure - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.01944 | biomass chp - back pressure - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp - back pressure - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp - back pressure - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.26 | biomass chp - back pressure - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.28 | biomass chp - back pressure - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | combustion air humidification | ELH_0009 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | combustion air humidification | ELH_0009 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | combustion air humidification | ELH_0009 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | combustion air humidification | ELH_0009 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | combustion air humidification | ELH_0009 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | combustion air humidification | ELH_0009 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | combustion air humidification | ELH_0009 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | combustion air humidification | ELH_0009 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 44448.9796 | biomass chp - back pressure - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0009 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 43810.956 | biomass chp - back pressure - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0009 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 42747.5832 | biomass chp - back pressure - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0009 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 41471.536 | biomass chp - back pressure - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0009 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 37537.0569 | biomass chp - back pressure - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0009 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 31475.8324 | biomass chp - back pressure - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0009 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 50829.2159 | biomass chp - back pressure - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0009 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 53274.9731 | biomass chp - back pressure - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0009 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | flue gas condensation | ELH_0009 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | flue gas condensation | ELH_0009 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | flue gas condensation | ELH_0009 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | flue gas condensation | ELH_0009 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | flue gas condensation | ELH_0009 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | flue gas condensation | ELH_0009 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | flue gas condensation | ELH_0009 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - wood chips - small | technology-specific data | flue gas condensation | ELH_0009 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.021267 | biomass chp - back pressure - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0009 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.021267 | biomass chp - back pressure - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0009 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.021267 | biomass chp - back pressure - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0009 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.021267 | biomass chp - back pressure - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0009 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.021267 | biomass chp - back pressure - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0009 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.010634 | biomass chp - back pressure - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0009 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.021267 | biomass chp - back pressure - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0009 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.021267 | biomass chp - back pressure - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0009 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.97318 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.97318 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.9726 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.97546 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.73 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.7 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.98 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.98 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0076
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.96585 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.96585 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.96524 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.96825 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.71 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.69 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.98 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.98 | biomass chp - back pressure - wood chips - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0009 | tk_tsd | manual_category_map | PAR_0077
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0102 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 0.98894 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.93577 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.89323 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.86133 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.70183 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.1591 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.2122 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.62739 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.61676 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.58485 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.56359 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.53169 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.43598 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.72309 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.76563 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.38281 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.37218 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.35091 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.31901 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.32965 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.26584 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.43598 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.44662 | biomass chp - back pressure - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.25 | biomass chp - back pressure - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.25 | biomass chp - back pressure - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.25 | biomass chp - back pressure - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.25 | biomass chp - back pressure - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.25 | biomass chp - back pressure - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.25 | biomass chp - back pressure - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | steam reheat | ELH_0009 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | steam reheat | ELH_0009 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | steam reheat | ELH_0009 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | steam reheat | ELH_0009 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | steam reheat | ELH_0009 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | steam reheat | ELH_0009 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | steam reheat | ELH_0009 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 0 | biomass chp - back pressure - wood chips - small | technology-specific data | steam reheat | ELH_0009 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.4462 | biomass chp - back pressure - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.4462 | biomass chp - back pressure - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.4462 | biomass chp - back pressure - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.4462 | biomass chp - back pressure - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.0102 | biomass chp - back pressure - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.8826 | biomass chp - back pressure - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.627 | biomass chp - back pressure - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.7439 | biomass chp - back pressure - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0009 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.032838 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.032669 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.032701 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.032701 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.024078 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.019262 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.036904 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.036921 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.51 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.51 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.52 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.52 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.67 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.67 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 4.5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 4 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5.5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5.5 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0016 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.31768 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.31837 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.31925 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.31925 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.29 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.29 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.42 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.42 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.3344 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.33512 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.33605 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.33605 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.32 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.32 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.44 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.44 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0016 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0016 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0016 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0016 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0016 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0016 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0016 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0016 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0016 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 267.52 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 268.1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 268.84 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 268.84 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 262.35 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 262.35 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 348.19 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 348.58 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0016 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0016 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0016 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0016 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0016 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0016 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0016 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0016 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.05 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.07 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0016 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp, 40/80 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0016 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1.2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0016 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2015 | 0.9825 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0016 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2020 | 0.9825 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0016 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2030 | 0.9825 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0016 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2050 | 0.9825 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0016 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2020 | 0.95625 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0016 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2050 | 0.9825 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0016 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2020 | 0.99125 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0016 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2050 | 0.99125 | biomass chp, 40/80 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0016 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 68055.854 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0016 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 65929.1085 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0016 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 62738.9904 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0016 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 57422.1268 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0016 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 56358.7541 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0016 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 44661.6542 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0016 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 76562.8357 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0016 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 75499.463 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0016 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.4564 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.3926 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.2756 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.0629 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.031 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.6695 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 2.8073 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 2.8286 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.3718 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.3398 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.2654 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.1591 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.1059 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.9145 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.5632 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.5738 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.0846 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.0527 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0.99957 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.90387 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0.9145 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.75499 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.2441 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.2548 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 1.829 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 1.829 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 1.8184 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 1.8184 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.4675 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.2867 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.0842 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.2544 | biomass chp, 40/80 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0016 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 12 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 12 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 12 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 12 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2020 | 12 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2050 | 12 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2020 | 12 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2050 | 12 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.15 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.15 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.15 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.15 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.15 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.15 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.15 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.15 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0016 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 2 | biomass chp, 40/80 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0016 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.0173 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.01664 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.016639 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.016639 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.13 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.13 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0016 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0016 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0016 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0016 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0016 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0016 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0016 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0016 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 22756.1762 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0016 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 22224.4898 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0016 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 21267.4544 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0016 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 19459.7207 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0016 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 18715.3598 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0016 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 14993.5553 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0016 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 25839.957 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0016 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 25414.6079 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0016 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0016 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0016 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0016 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0016 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0016 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0016 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0016 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0016 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0016 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0016 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0016 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0016 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0016 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0016 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0016 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0016 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.6682 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.66939 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.66847 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.66847 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.46 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.46 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.69 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.69 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.65148 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.65264 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.65167 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.65167 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.43 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.43 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.67 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.67 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0016 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 0.8188 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 0.79753 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.76563 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.69119 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.68056 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.56359 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 0.9464 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 0.9464 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.45725 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.44662 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.42535 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.38281 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.37218 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.30838 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.52105 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.53169 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.36155 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.35091 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.34028 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.30838 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.30838 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.25521 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.41472 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.42535 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.06 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0016 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0016 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0016 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0016 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0016 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0016 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0016 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0016 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.60612 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.61676 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.61676 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.61676 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.48915 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.43598 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.70183 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.75499 | biomass chp, 40/80 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0016 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.032976 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.032803 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.032834 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.032834 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.024257 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.019405 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.037051 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.037069 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.49 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.49 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.49 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.49 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.48 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.48 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.64 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.65 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 4.5 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 4 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5.5 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5.5 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | construction time [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0019 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.30038 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.30095 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.3018 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.3018 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.27 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.27 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.4 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.4 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.31619 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.31679 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.31769 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.31769 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.31 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.31 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.42 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.42 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0019 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0019 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0019 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0019 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0019 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0019 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0019 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0019 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | forced outage [] | ELH_0019 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 252.95 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 253.44 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 254.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 254.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 248.11 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 248.11 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 333.42 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 333.79 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0019 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0019 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0019 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0019 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0019 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0019 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0019 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0019 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.06 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.06 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.06 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.06 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.05 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.07 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.07 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0019 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp, 50/100 degree - back pressure - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0019 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1.2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | n2o [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | nox [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | particles [g/gj_i] | ELH_0019 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2015 | 0.9825 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0019 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2020 | 0.9825 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0019 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2030 | 0.9825 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0019 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2050 | 0.9825 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0019 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2020 | 0.95625 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0019 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2050 | 0.9825 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0019 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2020 | 0.99125 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0019 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2050 | 0.99125 | biomass chp, 50/100 degree - back pressure - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0019 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 72309.3448 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0019 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 70182.5994 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0019 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 66992.4812 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0019 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 61675.6176 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0019 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 59548.8722 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0019 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 47851.7723 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0019 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 81879.6993 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0019 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 79752.9539 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0019 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.5946 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.5308 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.4032 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.1799 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.148 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.7652 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 2.9668 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 2.9881 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.4462 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.4143 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.3398 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.2229 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.1697 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.96767 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.6589 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.6589 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.1484 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.1165 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.0634 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.95704 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0.9783 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.79753 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.3186 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.3186 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 1.829 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 1.8396 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 1.829 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 1.829 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.5525 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.3611 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.1055 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.2863 | biomass chp, 50/100 degree - back pressure - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0019 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 12 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 12 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 12 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 12 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2020 | 12 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2050 | 12 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2020 | 12 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2050 | 12 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.15 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0019 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 2 | biomass chp, 50/100 degree - back pressure - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0019 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.041302 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.039725 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.039721 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.039721 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.13 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.13 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0019 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0019 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0019 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0019 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0019 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0019 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0019 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | combustion air humidification | ELH_0019 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 22756.1762 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0019 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 22224.4898 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0019 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 21267.4544 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0019 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 19459.7207 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0019 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 18715.3598 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0019 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 14993.5553 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0019 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 25839.957 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0019 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 25414.6079 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0019 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0019 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0019 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0019 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0019 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0019 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0019 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0019 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | flue gas condensation | ELH_0019 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0019 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0019 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0019 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0019 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0019 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0019 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0019 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0019 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.6614 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.66365 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.66276 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.66276 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.47 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.47 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.69 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.69 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.64559 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.64781 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.64688 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.64688 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.43 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.43 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.67 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.67 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0019 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 0.8188 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 0.79753 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.76563 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.69119 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.68056 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.56359 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 0.9464 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 0.9464 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.45725 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.44662 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.42535 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.38281 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.37218 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.30838 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.52105 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.53169 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.36155 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.35091 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.34028 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.30838 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.30838 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.25521 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.41472 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.42535 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0019 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0019 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0019 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0019 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0019 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0019 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0019 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | steam reheat | ELH_0019 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.57422 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.58485 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.58485 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.58485 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.48915 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.43598 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.66992 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.72309 | biomass chp, 50/100 degree - back pressure - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0019 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.025131 | biomass chp - back pressure - wood pellets - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.025131 | biomass chp - back pressure - wood pellets - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.025143 | biomass chp - back pressure - wood pellets - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.025081 | biomass chp - back pressure - wood pellets - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.019147 | biomass chp - back pressure - wood pellets - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.015273 | biomass chp - back pressure - wood pellets - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.029424 | biomass chp - back pressure - wood pellets - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.03051 | biomass chp - back pressure - wood pellets - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.46 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.46 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.46 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.45 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.44 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.44 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.62 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.63 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5 | biomass chp - back pressure - wood pellets - medium | energy/technical data | construction time [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5 | biomass chp - back pressure - wood pellets - medium | energy/technical data | construction time [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5 | biomass chp - back pressure - wood pellets - medium | energy/technical data | construction time [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5 | biomass chp - back pressure - wood pellets - medium | energy/technical data | construction time [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2 | biomass chp - back pressure - wood pellets - medium | energy/technical data | construction time [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5 | biomass chp - back pressure - wood pellets - medium | energy/technical data | construction time [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3 | biomass chp - back pressure - wood pellets - medium | energy/technical data | construction time [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3 | biomass chp - back pressure - wood pellets - medium | energy/technical data | construction time [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0010 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.29303 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.29303 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.29389 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.2898 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.26 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.26 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.4 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.41 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.30845 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.30845 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.30936 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.30505 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.29 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.29 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.42 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.43 | biomass chp - back pressure - wood pellets - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0010 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | forced outage [] | ELH_0010 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | forced outage [] | ELH_0010 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | forced outage [] | ELH_0010 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | forced outage [] | ELH_0010 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | forced outage [] | ELH_0010 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | forced outage [] | ELH_0010 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | forced outage [] | ELH_0010 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | forced outage [] | ELH_0010 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 24.68 | biomass chp - back pressure - wood pellets - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 24.68 | biomass chp - back pressure - wood pellets - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 24.75 | biomass chp - back pressure - wood pellets - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 24.4 | biomass chp - back pressure - wood pellets - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 23.84 | biomass chp - back pressure - wood pellets - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 23.78 | biomass chp - back pressure - wood pellets - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 33.36 | biomass chp - back pressure - wood pellets - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 34.03 | biomass chp - back pressure - wood pellets - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp - back pressure - wood pellets - medium | energy/technical data | planned outage [weeks per year] | ELH_0010 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp - back pressure - wood pellets - medium | energy/technical data | planned outage [weeks per year] | ELH_0010 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp - back pressure - wood pellets - medium | energy/technical data | planned outage [weeks per year] | ELH_0010 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp - back pressure - wood pellets - medium | energy/technical data | planned outage [weeks per year] | ELH_0010 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp - back pressure - wood pellets - medium | energy/technical data | planned outage [weeks per year] | ELH_0010 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp - back pressure - wood pellets - medium | energy/technical data | planned outage [weeks per year] | ELH_0010 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp - back pressure - wood pellets - medium | energy/technical data | planned outage [weeks per year] | ELH_0010 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp - back pressure - wood pellets - medium | energy/technical data | planned outage [weeks per year] | ELH_0010 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.18 | biomass chp - back pressure - wood pellets - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.18 | biomass chp - back pressure - wood pellets - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.18 | biomass chp - back pressure - wood pellets - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.18 | biomass chp - back pressure - wood pellets - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.16 | biomass chp - back pressure - wood pellets - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.14 | biomass chp - back pressure - wood pellets - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.21 | biomass chp - back pressure - wood pellets - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.23 | biomass chp - back pressure - wood pellets - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0010 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp - back pressure - wood pellets - medium | energy/technical data | technical lifetime [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp - back pressure - wood pellets - medium | energy/technical data | technical lifetime [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp - back pressure - wood pellets - medium | energy/technical data | technical lifetime [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp - back pressure - wood pellets - medium | energy/technical data | technical lifetime [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp - back pressure - wood pellets - medium | energy/technical data | technical lifetime [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp - back pressure - wood pellets - medium | energy/technical data | technical lifetime [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp - back pressure - wood pellets - medium | energy/technical data | technical lifetime [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp - back pressure - wood pellets - medium | energy/technical data | technical lifetime [years] | ELH_0010 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0 | biomass chp - back pressure - wood pellets - medium | environment | ch4 [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | environment | ch4 [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0 | biomass chp - back pressure - wood pellets - medium | environment | ch4 [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | environment | ch4 [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | environment | ch4 [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | environment | ch4 [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | environment | ch4 [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | environment | ch4 [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2 | biomass chp - back pressure - wood pellets - medium | environment | n2o [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | environment | n2o [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1 | biomass chp - back pressure - wood pellets - medium | environment | n2o [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | environment | n2o [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | environment | n2o [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | environment | n2o [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3 | biomass chp - back pressure - wood pellets - medium | environment | n2o [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | environment | n2o [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 80 | biomass chp - back pressure - wood pellets - medium | environment | nox [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 50 | biomass chp - back pressure - wood pellets - medium | environment | nox [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 40 | biomass chp - back pressure - wood pellets - medium | environment | nox [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20 | biomass chp - back pressure - wood pellets - medium | environment | nox [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 40 | biomass chp - back pressure - wood pellets - medium | environment | nox [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10 | biomass chp - back pressure - wood pellets - medium | environment | nox [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 50 | biomass chp - back pressure - wood pellets - medium | environment | nox [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 40 | biomass chp - back pressure - wood pellets - medium | environment | nox [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2 | biomass chp - back pressure - wood pellets - medium | environment | particles [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3 | biomass chp - back pressure - wood pellets - medium | environment | particles [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3 | biomass chp - back pressure - wood pellets - medium | environment | particles [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3 | biomass chp - back pressure - wood pellets - medium | environment | particles [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1 | biomass chp - back pressure - wood pellets - medium | environment | particles [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1 | biomass chp - back pressure - wood pellets - medium | environment | particles [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2 | biomass chp - back pressure - wood pellets - medium | environment | particles [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | environment | particles [g/gj_i] | ELH_0010 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9825 | biomass chp - back pressure - wood pellets - medium | environment | so2 (degree of desulphuring) [] | ELH_0010 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9825 | biomass chp - back pressure - wood pellets - medium | environment | so2 (degree of desulphuring) [] | ELH_0010 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9825 | biomass chp - back pressure - wood pellets - medium | environment | so2 (degree of desulphuring) [] | ELH_0010 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.9825 | biomass chp - back pressure - wood pellets - medium | environment | so2 (degree of desulphuring) [] | ELH_0010 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.95625 | biomass chp - back pressure - wood pellets - medium | environment | so2 (degree of desulphuring) [] | ELH_0010 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9825 | biomass chp - back pressure - wood pellets - medium | environment | so2 (degree of desulphuring) [] | ELH_0010 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.99125 | biomass chp - back pressure - wood pellets - medium | environment | so2 (degree of desulphuring) [] | ELH_0010 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.99125 | biomass chp - back pressure - wood pellets - medium | environment | so2 (degree of desulphuring) [] | ELH_0010 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 136111.7079 | biomass chp - back pressure - wood pellets - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0010 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 131858.217 | biomass chp - back pressure - wood pellets - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0010 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 124414.608 | biomass chp - back pressure - wood pellets - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0010 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 114844.2535 | biomass chp - back pressure - wood pellets - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0010 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 110590.7627 | biomass chp - back pressure - wood pellets - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0010 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 86133.1902 | biomass chp - back pressure - wood pellets - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0010 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 153125.6714 | biomass chp - back pressure - wood pellets - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0010 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 148872.1805 | biomass chp - back pressure - wood pellets - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0010 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.2752 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.2008 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.0306 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.8817 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.6584 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.2012 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 3.775 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 3.9451 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.0948 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.0417 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.9353 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.8822 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.6589 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.3718 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.4032 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 2.5627 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.1803 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.1591 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.0953 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.99957 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.0102 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.82943 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.3611 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.393 | biomass chp - back pressure - wood pellets - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 1.9779 | biomass chp - back pressure - wood pellets - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 1.9779 | biomass chp - back pressure - wood pellets - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 1.9672 | biomass chp - back pressure - wood pellets - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 1.9991 | biomass chp - back pressure - wood pellets - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.5951 | biomass chp - back pressure - wood pellets - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.4143 | biomass chp - back pressure - wood pellets - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.265 | biomass chp - back pressure - wood pellets - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.4777 | biomass chp - back pressure - wood pellets - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0010 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8 | biomass chp - back pressure - wood pellets - medium | regulation ability | cold start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8 | biomass chp - back pressure - wood pellets - medium | regulation ability | cold start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8 | biomass chp - back pressure - wood pellets - medium | regulation ability | cold start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8 | biomass chp - back pressure - wood pellets - medium | regulation ability | cold start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8 | biomass chp - back pressure - wood pellets - medium | regulation ability | cold start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8 | biomass chp - back pressure - wood pellets - medium | regulation ability | cold start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8 | biomass chp - back pressure - wood pellets - medium | regulation ability | cold start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8 | biomass chp - back pressure - wood pellets - medium | regulation ability | cold start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.15 | biomass chp - back pressure - wood pellets - medium | regulation ability | minimum load (of full load) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.15 | biomass chp - back pressure - wood pellets - medium | regulation ability | minimum load (of full load) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.15 | biomass chp - back pressure - wood pellets - medium | regulation ability | minimum load (of full load) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.15 | biomass chp - back pressure - wood pellets - medium | regulation ability | minimum load (of full load) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.15 | biomass chp - back pressure - wood pellets - medium | regulation ability | minimum load (of full load) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.15 | biomass chp - back pressure - wood pellets - medium | regulation ability | minimum load (of full load) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.15 | biomass chp - back pressure - wood pellets - medium | regulation ability | minimum load (of full load) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.15 | biomass chp - back pressure - wood pellets - medium | regulation ability | minimum load (of full load) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.1 | biomass chp - back pressure - wood pellets - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.1 | biomass chp - back pressure - wood pellets - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.1 | biomass chp - back pressure - wood pellets - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.1 | biomass chp - back pressure - wood pellets - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.1 | biomass chp - back pressure - wood pellets - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.1 | biomass chp - back pressure - wood pellets - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.1 | biomass chp - back pressure - wood pellets - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.1 | biomass chp - back pressure - wood pellets - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0010 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 0.25 | biomass chp - back pressure - wood pellets - medium | regulation ability | warm start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 0.25 | biomass chp - back pressure - wood pellets - medium | regulation ability | warm start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 0.25 | biomass chp - back pressure - wood pellets - medium | regulation ability | warm start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 0.25 | biomass chp - back pressure - wood pellets - medium | regulation ability | warm start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2020 | 0.25 | biomass chp - back pressure - wood pellets - medium | regulation ability | warm start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2050 | 0.25 | biomass chp - back pressure - wood pellets - medium | regulation ability | warm start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2020 | 0.25 | biomass chp - back pressure - wood pellets - medium | regulation ability | warm start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2050 | 0.25 | biomass chp - back pressure - wood pellets - medium | regulation ability | warm start-up time [hours] | ELH_0010 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.01729 | biomass chp - back pressure - wood pellets - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.01729 | biomass chp - back pressure - wood pellets - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017288 | biomass chp - back pressure - wood pellets - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017298 | biomass chp - back pressure - wood pellets - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp - back pressure - wood pellets - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp - back pressure - wood pellets - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.11 | biomass chp - back pressure - wood pellets - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.13 | biomass chp - back pressure - wood pellets - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | combustion air humidification | ELH_0010 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | combustion air humidification | ELH_0010 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | combustion air humidification | ELH_0010 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | combustion air humidification | ELH_0010 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | combustion air humidification | ELH_0010 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | combustion air humidification | ELH_0010 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | combustion air humidification | ELH_0010 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | combustion air humidification | ELH_0010 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 42003.2223 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0010 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 40727.1751 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0010 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 38494.0924 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0010 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 35197.6369 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0010 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 34134.2642 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0010 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 26158.9689 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0010 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 47213.7487 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0010 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 45406.015 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0010 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | flue gas condensation | ELH_0010 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | flue gas condensation | ELH_0010 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | flue gas condensation | ELH_0010 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | flue gas condensation | ELH_0010 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | flue gas condensation | ELH_0010 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | flue gas condensation | ELH_0010 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | flue gas condensation | ELH_0010 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | flue gas condensation | ELH_0010 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0010 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0010 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0010 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0010 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0010 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0010 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0010 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0010 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.69234 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.69234 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.69144 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.69571 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.47 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.45 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.73 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.73 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.67691 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.67691 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.67597 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.68046 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.44 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.42 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.71 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.71 | biomass chp - back pressure - wood pellets - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0010 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0102 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 0.98894 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.93577 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.8826 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.8188 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.66992 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.1591 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.2016 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.64866 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.62739 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.59549 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.57422 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.51042 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.41472 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.74436 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.77626 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.36155 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.35091 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.34028 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.30838 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.30838 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.25521 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.42535 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.42535 | biomass chp - back pressure - wood pellets - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.06 | biomass chp - back pressure - wood pellets - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.06 | biomass chp - back pressure - wood pellets - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.06 | biomass chp - back pressure - wood pellets - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.06 | biomass chp - back pressure - wood pellets - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.06 | biomass chp - back pressure - wood pellets - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.06 | biomass chp - back pressure - wood pellets - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | steam reheat | ELH_0010 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | steam reheat | ELH_0010 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | steam reheat | ELH_0010 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | steam reheat | ELH_0010 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | steam reheat | ELH_0010 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp - back pressure - wood pellets - medium | technology-specific data | steam reheat | ELH_0010 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | steam reheat | ELH_0010 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp - back pressure - wood pellets - medium | technology-specific data | steam reheat | ELH_0010 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.60612 | biomass chp - back pressure - wood pellets - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.60612 | biomass chp - back pressure - wood pellets - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.60612 | biomass chp - back pressure - wood pellets - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.60612 | biomass chp - back pressure - wood pellets - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.48915 | biomass chp - back pressure - wood pellets - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.43598 | biomass chp - back pressure - wood pellets - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.70183 | biomass chp - back pressure - wood pellets - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.75499 | biomass chp - back pressure - wood pellets - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0010 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.022902 | biomass chp - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.022902 | biomass chp - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.022911 | biomass chp - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.02287 | biomass chp - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.01744 | biomass chp - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.013926 | biomass chp - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.025032 | biomass chp - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.025037 | biomass chp - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.18 | biomass chp - boiler - wood pellets - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.18 | biomass chp - boiler - wood pellets - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.19 | biomass chp - boiler - wood pellets - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.18 | biomass chp - boiler - wood pellets - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.18 | biomass chp - boiler - wood pellets - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.18 | biomass chp - boiler - wood pellets - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.19 | biomass chp - boiler - wood pellets - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.19 | biomass chp - boiler - wood pellets - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0014
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5 | biomass chp - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5 | biomass chp - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5 | biomass chp - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5 | biomass chp - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp - boiler - wood pellets - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0011 | tk_etd | manual_category_map | PAR_0027
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.1464 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.1464 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.14683 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.14466 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.13 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.13 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.15 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.15 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.1541 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.1541 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.15456 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.15227 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.15 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.14 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.16 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.16 | biomass chp - boiler - wood pellets - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0011 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0011 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0011 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0011 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0011 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0011 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0011 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0011 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0011 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 3.08 | biomass chp - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 3.08 | biomass chp - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 3.09 | biomass chp - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 3.05 | biomass chp - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 3 | biomass chp - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 2.95 | biomass chp - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 3.12 | biomass chp - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 3.12 | biomass chp - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0011 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0011 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0011 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0011 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0011 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0011 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0011 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0011 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.49 | biomass chp - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.49 | biomass chp - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.49 | biomass chp - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.49 | biomass chp - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.41 | biomass chp - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.37 | biomass chp - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.56 | biomass chp - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.62 | biomass chp - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0011 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0011 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 0 | biomass chp - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 0 | biomass chp - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 0 | biomass chp - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 0 | biomass chp - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 0 | biomass chp - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0 | biomass chp - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 0 | biomass chp - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 0 | biomass chp - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 1.2 | biomass chp - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 1 | biomass chp - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 1 | biomass chp - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 1 | biomass chp - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 1 | biomass chp - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0 | biomass chp - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 3 | biomass chp - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 1 | biomass chp - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 90 | biomass chp - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 50 | biomass chp - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 40 | biomass chp - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 30 | biomass chp - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 40 | biomass chp - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 20 | biomass chp - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 70 | biomass chp - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 40 | biomass chp - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 2 | biomass chp - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 0.3 | biomass chp - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 0.3 | biomass chp - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 0.3 | biomass chp - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 0.1 | biomass chp - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0.1 | biomass chp - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 2 | biomass chp - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 1 | biomass chp - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0011 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2015 | 0.9825 | biomass chp - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0011 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2020 | 0.9825 | biomass chp - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0011 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2030 | 0.9825 | biomass chp - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0011 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2050 | 0.9825 | biomass chp - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0011 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | lower | 2020 | 0.95625 | biomass chp - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0011 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | lower | 2050 | 0.9825 | biomass chp - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0011 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | upper | 2020 | 0.99125 | biomass chp - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0011 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | upper | 2050 | 0.99125 | biomass chp - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0011 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 292427.4975 | biomass chp - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0011 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 288174.0066 | biomass chp - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0011 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 277540.2794 | biomass chp - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0011 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 269033.2977 | biomass chp - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0011 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 246702.4706 | biomass chp - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0011 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 204167.5619 | biomass chp - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0011 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 333899.0335 | biomass chp - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0011 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 345596.1334 | biomass chp - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0011 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2015 | 6.6142 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2020 | 6.444 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2030 | 6.1144 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2050 | 5.8911 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2020 | 5.6146 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2050 | 4.6576 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2020 | 7.6031 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2050 | 8.0285 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 4.3173 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 4.211 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 3.9876 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 3.9345 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 3.6686 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 3.0412 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 4.9553 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 5.3381 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.2969 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.2437 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.1267 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.946 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.9566 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.6163 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.6478 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 2.701 | biomass chp - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.1365 | biomass chp - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.1365 | biomass chp - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.1259 | biomass chp - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.1897 | biomass chp - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.1795 | biomass chp - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 2.8392 | biomass chp - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 4.7107 | biomass chp - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 5.1467 | biomass chp - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0011 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5 | biomass chp - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5 | biomass chp - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5 | biomass chp - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5 | biomass chp - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5 | biomass chp - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5 | biomass chp - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5 | biomass chp - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5 | biomass chp - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2015 | 0.2 | biomass chp - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2020 | 0.2 | biomass chp - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2030 | 0.2 | biomass chp - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2050 | 0.2 | biomass chp - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2020 | 0.2 | biomass chp - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2050 | 0.2 | biomass chp - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2020 | 0.2 | biomass chp - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2050 | 0.2 | biomass chp - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.1 | biomass chp - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.1 | biomass chp - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.1 | biomass chp - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.1 | biomass chp - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.1 | biomass chp - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.1 | biomass chp - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.1 | biomass chp - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.1 | biomass chp - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0011 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 0.25 | biomass chp - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 0.25 | biomass chp - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 0.25 | biomass chp - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 0.25 | biomass chp - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 0.25 | biomass chp - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 0.25 | biomass chp - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 0.25 | biomass chp - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 0.25 | biomass chp - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0011 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.01729 | biomass chp - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.01729 | biomass chp - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017288 | biomass chp - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017298 | biomass chp - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.11 | biomass chp - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.13 | biomass chp - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0011 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0011 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0011 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0011 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0011 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0011 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0011 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0011 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 45193.3405 | biomass chp - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0011 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 44342.6423 | biomass chp - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0011 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 42853.9205 | biomass chp - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0011 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 40939.8496 | biomass chp - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0011 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 37962.406 | biomass chp - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0011 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 31050.4834 | biomass chp - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0011 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 51467.2395 | biomass chp - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0011 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 52636.9495 | biomass chp - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0011 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0011 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0011 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0011 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0011 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0011 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0011 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0011 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0011 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0011 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0011 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0011 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0011 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0011 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0011 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0011 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0011 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.84204 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.84204 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.84158 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.84385 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.74 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.72 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.86 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.86 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.83433 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.83433 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.83386 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.83624 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.72 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.71 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.85 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.85 | biomass chp - boiler - wood pellets - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0011 | tk_tsd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2015 | 1.0208 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2020 | 0.98894 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2030 | 0.9464 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2050 | 0.89323 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | lower | 2020 | 0.86133 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | lower | 2050 | 0.71246 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | upper | 2020 | 1.1697 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | upper | 2050 | 1.2229 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.65929 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.64866 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.61676 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.59549 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.56359 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.45725 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.76563 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.80816 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.35091 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.34028 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.32965 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.29774 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.29774 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.24458 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.40408 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.41472 | biomass chp - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.06 | biomass chp - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.06 | biomass chp - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.06 | biomass chp - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.06 | biomass chp - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.06 | biomass chp - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.06 | biomass chp - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | steam reheat | ELH_0011 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | steam reheat | ELH_0011 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | steam reheat | ELH_0011 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | steam reheat | ELH_0011 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | steam reheat | ELH_0011 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | steam reheat | ELH_0011 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | steam reheat | ELH_0011 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 0 | biomass chp - boiler - wood pellets - small | technology-specific data | steam reheat | ELH_0011 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.63802 | biomass chp - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.63802 | biomass chp - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.63802 | biomass chp - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.63802 | biomass chp - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.48915 | biomass chp - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.43598 | biomass chp - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.72309 | biomass chp - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.7869 | biomass chp - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0011 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.028381 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.028381 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.028399 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.028399 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.020912 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017287 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.031371 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.032976 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.45 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.45 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.46 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.46 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.43 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.44 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.6 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.61 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cb coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2.5 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3.5 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3.5 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | cv coefficient (40°c/80°c) | ELH_0014 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.29936 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.29936 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.30028 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.30028 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.26 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.27 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.41 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.31511 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.31511 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.31609 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.31609 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.29 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.42 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.43 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0014 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0014 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0014 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0014 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0014 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0014 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0014 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0014 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0014 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 41.59 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 41.59 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 41.72 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 41.72 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 39.48 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 40.62 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 54.62 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 55.84 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0014 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0014 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0014 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0014 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0014 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0014 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0014 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0014 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.24 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.24 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.24 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.24 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.2 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.18 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.28 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.3 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0014 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp, 40/80 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0014 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2 | biomass chp, 40/80 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3 | biomass chp, 40/80 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 40 | biomass chp, 40/80 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 30 | biomass chp, 40/80 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 30 | biomass chp, 40/80 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20 | biomass chp, 40/80 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20 | biomass chp, 40/80 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10 | biomass chp, 40/80 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 40 | biomass chp, 40/80 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 30 | biomass chp, 40/80 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0.3 | biomass chp, 40/80 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3 | biomass chp, 40/80 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3 | biomass chp, 40/80 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3 | biomass chp, 40/80 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1 | biomass chp, 40/80 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1 | biomass chp, 40/80 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0014 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9545 | biomass chp, 40/80 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0014 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9636 | biomass chp, 40/80 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0014 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9909 | biomass chp, 40/80 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0014 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.99818 | biomass chp, 40/80 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0014 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.909 | biomass chp, 40/80 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0014 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9545 | biomass chp, 40/80 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0014 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.99818 | biomass chp, 40/80 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0014 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.99909 | biomass chp, 40/80 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0014 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2015 | 133984.9625 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0014 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2020 | 129731.4716 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0014 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2030 | 122287.8626 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0014 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2050 | 109527.39 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0014 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2020 | 109527.39 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0014 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2050 | 84006.4447 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0014 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2020 | 150998.926 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0014 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2050 | 141428.5715 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0014 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.6793 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.5942 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.4134 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.0944 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.0412 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.4989 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.2216 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.2429 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2015 | 2.2756 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2020 | 2.2224 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2030 | 2.1055 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2050 | 1.9141 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2020 | 1.8396 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2050 | 1.5206 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2020 | 2.6053 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2050 | 2.6159 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2015 | 1.4143 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2020 | 1.3718 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2030 | 1.3079 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2050 | 1.1803 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2020 | 1.2016 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2050 | 0.9783 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2020 | 1.6163 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2050 | 1.627 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 2.2437 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 2.2437 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 2.2331 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 2.2331 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.7227 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.51 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.5521 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.7435 | biomass chp, 40/80 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0014 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.4 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0014 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2020 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2050 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2020 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2050 | 2 | biomass chp, 40/80 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0014 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.017679 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.017679 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017677 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017677 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.15 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.15 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0014 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0014 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0014 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0014 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0014 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0014 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0014 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0014 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2015 | 42215.8969 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0014 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2020 | 40939.8496 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0014 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2030 | 38600.4296 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0014 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2050 | 34453.276 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0014 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2020 | 34559.6133 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0014 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2050 | 26477.9807 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0014 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2020 | 47426.4232 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0014 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2050 | 44555.3169 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0014 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0014 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0014 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0014 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0014 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0014 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0014 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0014 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0014 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.063802 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0014 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.063802 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0014 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.063802 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0014 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.053169 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0014 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.063802 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0014 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.053169 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0014 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.074436 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0014 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.08507 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0014 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.70927 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.70927 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.70831 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.70831 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.48 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.47 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.74 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.73 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.69351 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.69351 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.69251 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.69251 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.45 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.44 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.72 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.71 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0014 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.1591 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.1378 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.074 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.9783 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.95704 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.7869 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.3292 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.3398 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.71246 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.70183 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.66992 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.60612 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.58485 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.47852 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.8188 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.82943 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.44662 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.43598 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.41472 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.37218 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.38281 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.30838 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.51042 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.51042 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.09 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.09 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.09 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.09 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.09 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.09 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0014 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0014 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0014 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0014 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0014 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0014 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0014 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0014 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.70183 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.70183 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.70183 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.70183 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.47852 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.80816 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.87197 | biomass chp, 40/80 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0014 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.028554 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.028554 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.028572 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.028572 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.021147 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017474 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.031556 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.03316 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.43 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0015
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.43 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0015
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.43 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0015
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.43 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0015
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.41 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0015
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.42 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0015
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.57 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0015
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.59 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0015
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2.5 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3.5 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3.5 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | construction time [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0028
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0028
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0028
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0028
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0028
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0028
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0028
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0017 | tk_etd | manual_category_map | PAR_0028
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.28061 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.28061 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.2815 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.2815 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.25 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.25 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.38 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.39 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.29538 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.29538 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.29632 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.29632 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.27 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.28 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.41 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0017 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0017 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0017 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0017 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0017 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0017 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0017 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0017 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | forced outage [] | ELH_0017 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 38.99 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 38.99 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 39.11 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 39.11 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 36.88 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 38.07 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 52.01 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 53.28 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0017 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0017 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0017 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0017 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0017 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0017 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0017 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | planned outage [weeks per year] | ELH_0017 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.26 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.26 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.26 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.26 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.22 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.19 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.29 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.32 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0017 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp, 50/100 degree - back pressure - straw - large | energy/technical data | technical lifetime [years] | ELH_0017 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | ch4 [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2 | biomass chp, 50/100 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3 | biomass chp, 50/100 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | environment | n2o [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 40 | biomass chp, 50/100 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 30 | biomass chp, 50/100 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 30 | biomass chp, 50/100 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20 | biomass chp, 50/100 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20 | biomass chp, 50/100 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10 | biomass chp, 50/100 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 40 | biomass chp, 50/100 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 30 | biomass chp, 50/100 degree - back pressure - straw - large | environment | nox [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0.3 | biomass chp, 50/100 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3 | biomass chp, 50/100 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3 | biomass chp, 50/100 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3 | biomass chp, 50/100 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1 | biomass chp, 50/100 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1 | biomass chp, 50/100 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | environment | particles [g/gj_i] | ELH_0017 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9545 | biomass chp, 50/100 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0017 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9636 | biomass chp, 50/100 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0017 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9909 | biomass chp, 50/100 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0017 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.99818 | biomass chp, 50/100 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0017 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.909 | biomass chp, 50/100 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0017 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9545 | biomass chp, 50/100 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0017 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.99818 | biomass chp, 50/100 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0017 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.99909 | biomass chp, 50/100 degree - back pressure - straw - large | environment | so2 (degree of desulphuring) [] | ELH_0017 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2015 | 142491.9442 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0017 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2020 | 138238.4533 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0017 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2030 | 130794.8443 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0017 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2050 | 115907.6263 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0017 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2020 | 116970.999 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0017 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2050 | 89323.3083 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0017 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2020 | 160569.2804 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0017 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2050 | 150998.926 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0017 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.9345 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.8388 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.6367 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.3071 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.2433 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.6584 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.5087 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.53 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2015 | 2.4245 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2020 | 2.3713 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2030 | 2.2544 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2050 | 2.0417 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2020 | 1.9672 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2050 | 1.6163 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2020 | 2.7754 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2050 | 2.786 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2015 | 1.4994 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2020 | 1.4675 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2030 | 1.393 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2050 | 1.2548 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2020 | 1.276 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2050 | 1.0421 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2020 | 1.7333 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2050 | 1.7333 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 2.2756 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 2.2756 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 2.2756 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 2.2756 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.8396 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.6163 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.6159 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.8179 | biomass chp, 50/100 degree - back pressure - straw - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0017 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | cold start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.4 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | minimum load (of full load) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0171
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0017 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2020 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2050 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2020 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2050 | 2 | biomass chp, 50/100 degree - back pressure - straw - large | regulation ability | warm start-up time [hours] | ELH_0017 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.042201 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.042201 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.042197 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.042197 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.04 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.15 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.15 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0017 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0017 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0017 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0017 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0017 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0017 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0017 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | combustion air humidification | ELH_0017 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2015 | 42215.8969 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0017 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2020 | 40939.8496 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0017 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2030 | 38600.4296 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0017 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2050 | 34453.276 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0017 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2020 | 34559.6133 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0017 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2050 | 26477.9807 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0017 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2020 | 47426.4232 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0017 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2050 | 44555.3169 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0017 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0017 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0017 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0017 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0017 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0017 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0017 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0017 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | flue gas condensation | ELH_0017 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.063802 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0017 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.063802 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0017 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.063802 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0017 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.053169 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0017 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.063802 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0017 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.053169 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0017 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.074436 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0017 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.08507 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0017 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.70348 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.70348 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.70257 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.70257 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.49 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.49 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.73 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.72 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, annual average) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.68871 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.68871 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.68775 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.68775 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.47 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.46 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.71 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.7 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | heat efficiency (net, name plate) [] | ELH_0017 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.1591 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.1378 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.074 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.9783 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.95704 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.7869 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.3292 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.3398 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.71246 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.70183 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.66992 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.60612 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.58485 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.47852 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.8188 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.82943 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.44662 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.43598 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.41472 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.37218 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.38281 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.30838 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.51042 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.51042 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.06 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.06 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.06 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.06 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.06 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.06 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0017 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0017 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0017 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0017 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0017 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0017 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0017 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | steam reheat | ELH_0017 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.66992 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.66992 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.66992 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.66992 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.47852 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.77626 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.84006 | biomass chp, 50/100 degree - back pressure - straw - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0017 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.02847 | biomass chp - back pressure - straw - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.02847 | biomass chp - back pressure - straw - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.028488 | biomass chp - back pressure - straw - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.028396 | biomass chp - back pressure - straw - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.02091 | biomass chp - back pressure - straw - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017285 | biomass chp - back pressure - straw - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.031682 | biomass chp - back pressure - straw - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.032112 | biomass chp - back pressure - straw - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.46 | biomass chp - back pressure - straw - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.46 | biomass chp - back pressure - straw - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.46 | biomass chp - back pressure - straw - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.45 | biomass chp - back pressure - straw - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.43 | biomass chp - back pressure - straw - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.44 | biomass chp - back pressure - straw - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.47 | biomass chp - back pressure - straw - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.47 | biomass chp - back pressure - straw - medium | energy/technical data | cb coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5 | biomass chp - back pressure - straw - medium | energy/technical data | construction time [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5 | biomass chp - back pressure - straw - medium | energy/technical data | construction time [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5 | biomass chp - back pressure - straw - medium | energy/technical data | construction time [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5 | biomass chp - back pressure - straw - medium | energy/technical data | construction time [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2 | biomass chp - back pressure - straw - medium | energy/technical data | construction time [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5 | biomass chp - back pressure - straw - medium | energy/technical data | construction time [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3 | biomass chp - back pressure - straw - medium | energy/technical data | construction time [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3 | biomass chp - back pressure - straw - medium | energy/technical data | construction time [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp - back pressure - straw - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp - back pressure - straw - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp - back pressure - straw - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp - back pressure - straw - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp - back pressure - straw - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp - back pressure - straw - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp - back pressure - straw - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp - back pressure - straw - medium | energy/technical data | cv coefficient (40°c/80°c) | ELH_0006 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.30027 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.30027 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.3012 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.29677 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.26 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.27 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.31 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.31 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.31607 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.31607 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.31706 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.31239 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.29 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.3 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.33 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.33 | biomass chp - back pressure - straw - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0006 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.04 | biomass chp - back pressure - straw - medium | energy/technical data | forced outage [] | ELH_0006 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.04 | biomass chp - back pressure - straw - medium | energy/technical data | forced outage [] | ELH_0006 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.04 | biomass chp - back pressure - straw - medium | energy/technical data | forced outage [] | ELH_0006 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.04 | biomass chp - back pressure - straw - medium | energy/technical data | forced outage [] | ELH_0006 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.04 | biomass chp - back pressure - straw - medium | energy/technical data | forced outage [] | ELH_0006 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.04 | biomass chp - back pressure - straw - medium | energy/technical data | forced outage [] | ELH_0006 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.04 | biomass chp - back pressure - straw - medium | energy/technical data | forced outage [] | ELH_0006 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.04 | biomass chp - back pressure - straw - medium | energy/technical data | forced outage [] | ELH_0006 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 25.29 | biomass chp - back pressure - straw - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 25.29 | biomass chp - back pressure - straw - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 25.36 | biomass chp - back pressure - straw - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 24.99 | biomass chp - back pressure - straw - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 23.67 | biomass chp - back pressure - straw - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 24.33 | biomass chp - back pressure - straw - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 25.72 | biomass chp - back pressure - straw - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 25.84 | biomass chp - back pressure - straw - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 4 | biomass chp - back pressure - straw - medium | energy/technical data | planned outage [weeks per year] | ELH_0006 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 4 | biomass chp - back pressure - straw - medium | energy/technical data | planned outage [weeks per year] | ELH_0006 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 4 | biomass chp - back pressure - straw - medium | energy/technical data | planned outage [weeks per year] | ELH_0006 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 4 | biomass chp - back pressure - straw - medium | energy/technical data | planned outage [weeks per year] | ELH_0006 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 3.4 | biomass chp - back pressure - straw - medium | energy/technical data | planned outage [weeks per year] | ELH_0006 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 3 | biomass chp - back pressure - straw - medium | energy/technical data | planned outage [weeks per year] | ELH_0006 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 4.6 | biomass chp - back pressure - straw - medium | energy/technical data | planned outage [weeks per year] | ELH_0006 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 5 | biomass chp - back pressure - straw - medium | energy/technical data | planned outage [weeks per year] | ELH_0006 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.28 | biomass chp - back pressure - straw - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.28 | biomass chp - back pressure - straw - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.28 | biomass chp - back pressure - straw - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.28 | biomass chp - back pressure - straw - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.24 | biomass chp - back pressure - straw - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.21 | biomass chp - back pressure - straw - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.32 | biomass chp - back pressure - straw - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.35 | biomass chp - back pressure - straw - medium | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0006 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp - back pressure - straw - medium | energy/technical data | technical lifetime [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp - back pressure - straw - medium | energy/technical data | technical lifetime [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp - back pressure - straw - medium | energy/technical data | technical lifetime [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp - back pressure - straw - medium | energy/technical data | technical lifetime [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp - back pressure - straw - medium | energy/technical data | technical lifetime [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp - back pressure - straw - medium | energy/technical data | technical lifetime [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp - back pressure - straw - medium | energy/technical data | technical lifetime [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp - back pressure - straw - medium | energy/technical data | technical lifetime [years] | ELH_0006 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0 | biomass chp - back pressure - straw - medium | environment | ch4 [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0 | biomass chp - back pressure - straw - medium | environment | ch4 [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0 | biomass chp - back pressure - straw - medium | environment | ch4 [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0 | biomass chp - back pressure - straw - medium | environment | ch4 [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0 | biomass chp - back pressure - straw - medium | environment | ch4 [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp - back pressure - straw - medium | environment | ch4 [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0 | biomass chp - back pressure - straw - medium | environment | ch4 [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0 | biomass chp - back pressure - straw - medium | environment | ch4 [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2 | biomass chp - back pressure - straw - medium | environment | n2o [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1 | biomass chp - back pressure - straw - medium | environment | n2o [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1 | biomass chp - back pressure - straw - medium | environment | n2o [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1 | biomass chp - back pressure - straw - medium | environment | n2o [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1 | biomass chp - back pressure - straw - medium | environment | n2o [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0 | biomass chp - back pressure - straw - medium | environment | n2o [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3 | biomass chp - back pressure - straw - medium | environment | n2o [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp - back pressure - straw - medium | environment | n2o [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 90 | biomass chp - back pressure - straw - medium | environment | nox [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 70 | biomass chp - back pressure - straw - medium | environment | nox [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 50 | biomass chp - back pressure - straw - medium | environment | nox [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 30 | biomass chp - back pressure - straw - medium | environment | nox [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20 | biomass chp - back pressure - straw - medium | environment | nox [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10 | biomass chp - back pressure - straw - medium | environment | nox [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 90 | biomass chp - back pressure - straw - medium | environment | nox [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 50 | biomass chp - back pressure - straw - medium | environment | nox [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2 | biomass chp - back pressure - straw - medium | environment | particles [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3 | biomass chp - back pressure - straw - medium | environment | particles [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3 | biomass chp - back pressure - straw - medium | environment | particles [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3 | biomass chp - back pressure - straw - medium | environment | particles [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1 | biomass chp - back pressure - straw - medium | environment | particles [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1 | biomass chp - back pressure - straw - medium | environment | particles [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2 | biomass chp - back pressure - straw - medium | environment | particles [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1 | biomass chp - back pressure - straw - medium | environment | particles [g/gj_i] | ELH_0006 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9545 | biomass chp - back pressure - straw - medium | environment | so2 (degree of desulphuring) [] | ELH_0006 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9636 | biomass chp - back pressure - straw - medium | environment | so2 (degree of desulphuring) [] | ELH_0006 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9909 | biomass chp - back pressure - straw - medium | environment | so2 (degree of desulphuring) [] | ELH_0006 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.99818 | biomass chp - back pressure - straw - medium | environment | so2 (degree of desulphuring) [] | ELH_0006 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.909 | biomass chp - back pressure - straw - medium | environment | so2 (degree of desulphuring) [] | ELH_0006 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9545 | biomass chp - back pressure - straw - medium | environment | so2 (degree of desulphuring) [] | ELH_0006 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.99818 | biomass chp - back pressure - straw - medium | environment | so2 (degree of desulphuring) [] | ELH_0006 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.99909 | biomass chp - back pressure - straw - medium | environment | so2 (degree of desulphuring) [] | ELH_0006 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | ctrl | 2015 | 156315.7895 | biomass chp - back pressure - straw - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0006 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | ctrl | 2020 | 152062.2987 | biomass chp - back pressure - straw - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0006 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | ctrl | 2030 | 142491.9442 | biomass chp - back pressure - straw - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0006 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | ctrl | 2050 | 131858.217 | biomass chp - back pressure - straw - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0006 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | lower | 2020 | 127604.7262 | biomass chp - back pressure - straw - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0006 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | lower | 2050 | 101020.4082 | biomass chp - back pressure - straw - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0006 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | upper | 2020 | 178646.6166 | biomass chp - back pressure - straw - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0006 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | upper | 2050 | 170139.6349 | biomass chp - back pressure - straw - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0006 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.8919 | biomass chp - back pressure - straw - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.7962 | biomass chp - back pressure - straw - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.6048 | biomass chp - back pressure - straw - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.4134 | biomass chp - back pressure - straw - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.1901 | biomass chp - back pressure - straw - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.7435 | biomass chp - back pressure - straw - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.5831 | biomass chp - back pressure - straw - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.6682 | biomass chp - back pressure - straw - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.3607 | biomass chp - back pressure - straw - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.2969 | biomass chp - back pressure - straw - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.1799 | biomass chp - back pressure - straw - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.1055 | biomass chp - back pressure - straw - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 1.8822 | biomass chp - back pressure - straw - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.6589 | biomass chp - back pressure - straw - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 2.8073 | biomass chp - back pressure - straw - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 2.8711 | biomass chp - back pressure - straw - medium | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 1.5419 | biomass chp - back pressure - straw - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 1.4994 | biomass chp - back pressure - straw - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 1.4249 | biomass chp - back pressure - straw - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 1.3079 | biomass chp - back pressure - straw - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 1.3079 | biomass chp - back pressure - straw - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.0846 | biomass chp - back pressure - straw - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 1.7652 | biomass chp - back pressure - straw - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 1.8077 | biomass chp - back pressure - straw - medium | financial data | nominal investment (installation) [meur/mw_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | ctrl | 2015 | 2.2331 | biomass chp - back pressure - straw - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | ctrl | 2020 | 2.2331 | biomass chp - back pressure - straw - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | ctrl | 2030 | 2.2224 | biomass chp - back pressure - straw - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | ctrl | 2050 | 2.2544 | biomass chp - back pressure - straw - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | lower | 2020 | 1.712 | biomass chp - back pressure - straw - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | lower | 2050 | 1.5313 | biomass chp - back pressure - straw - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | upper | 2020 | 2.5415 | biomass chp - back pressure - straw - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | upper | 2050 | 2.7754 | biomass chp - back pressure - straw - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0006 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8 | biomass chp - back pressure - straw - medium | regulation ability | cold start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8 | biomass chp - back pressure - straw - medium | regulation ability | cold start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8 | biomass chp - back pressure - straw - medium | regulation ability | cold start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8 | biomass chp - back pressure - straw - medium | regulation ability | cold start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8 | biomass chp - back pressure - straw - medium | regulation ability | cold start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8 | biomass chp - back pressure - straw - medium | regulation ability | cold start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8 | biomass chp - back pressure - straw - medium | regulation ability | cold start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8 | biomass chp - back pressure - straw - medium | regulation ability | cold start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.4 | biomass chp - back pressure - straw - medium | regulation ability | minimum load (of full load) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.4 | biomass chp - back pressure - straw - medium | regulation ability | minimum load (of full load) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.4 | biomass chp - back pressure - straw - medium | regulation ability | minimum load (of full load) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.4 | biomass chp - back pressure - straw - medium | regulation ability | minimum load (of full load) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.4 | biomass chp - back pressure - straw - medium | regulation ability | minimum load (of full load) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.4 | biomass chp - back pressure - straw - medium | regulation ability | minimum load (of full load) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.4 | biomass chp - back pressure - straw - medium | regulation ability | minimum load (of full load) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.4 | biomass chp - back pressure - straw - medium | regulation ability | minimum load (of full load) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp - back pressure - straw - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp - back pressure - straw - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp - back pressure - straw - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp - back pressure - straw - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp - back pressure - straw - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp - back pressure - straw - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp - back pressure - straw - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp - back pressure - straw - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0006 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 2 | biomass chp - back pressure - straw - medium | regulation ability | warm start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 2 | biomass chp - back pressure - straw - medium | regulation ability | warm start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 2 | biomass chp - back pressure - straw - medium | regulation ability | warm start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 2 | biomass chp - back pressure - straw - medium | regulation ability | warm start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2020 | 2 | biomass chp - back pressure - straw - medium | regulation ability | warm start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2050 | 2 | biomass chp - back pressure - straw - medium | regulation ability | warm start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2020 | 2 | biomass chp - back pressure - straw - medium | regulation ability | warm start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2050 | 2 | biomass chp - back pressure - straw - medium | regulation ability | warm start-up time [hours] | ELH_0006 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.017669 | biomass chp - back pressure - straw - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.017669 | biomass chp - back pressure - straw - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017667 | biomass chp - back pressure - straw - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017677 | biomass chp - back pressure - straw - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp - back pressure - straw - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp - back pressure - straw - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.15 | biomass chp - back pressure - straw - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.15 | biomass chp - back pressure - straw - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | combustion air humidification | ELH_0006 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | combustion air humidification | ELH_0006 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | combustion air humidification | ELH_0006 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | combustion air humidification | ELH_0006 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | combustion air humidification | ELH_0006 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | combustion air humidification | ELH_0006 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | combustion air humidification | ELH_0006 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | combustion air humidification | ELH_0006 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2015 | 49553.1686 | biomass chp - back pressure - straw - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0006 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2020 | 48064.4468 | biomass chp - back pressure - straw - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0006 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2030 | 45299.6778 | biomass chp - back pressure - straw - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0006 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2050 | 41152.5242 | biomass chp - back pressure - straw - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0006 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2020 | 40408.1633 | biomass chp - back pressure - straw - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0006 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2050 | 31475.8324 | biomass chp - back pressure - straw - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0006 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2020 | 56358.754 | biomass chp - back pressure - straw - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0006 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2050 | 53062.2986 | biomass chp - back pressure - straw - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0006 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | flue gas condensation | ELH_0006 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | flue gas condensation | ELH_0006 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | flue gas condensation | ELH_0006 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | flue gas condensation | ELH_0006 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | flue gas condensation | ELH_0006 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | flue gas condensation | ELH_0006 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | flue gas condensation | ELH_0006 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - straw - medium | technology-specific data | flue gas condensation | ELH_0006 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.074436 | biomass chp - back pressure - straw - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0006 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.074436 | biomass chp - back pressure - straw - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0006 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.063802 | biomass chp - back pressure - straw - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0006 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.063802 | biomass chp - back pressure - straw - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0006 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.063802 | biomass chp - back pressure - straw - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0006 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.053169 | biomass chp - back pressure - straw - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0006 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.08507 | biomass chp - back pressure - straw - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0006 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.08507 | biomass chp - back pressure - straw - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0006 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.70205 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.70205 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.70107 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.70573 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.56 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.56 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.74 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.73 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, annual average) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.68625 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.68625 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.68522 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.69011 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.53 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.53 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.72 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.71 | biomass chp - back pressure - straw - medium | technology-specific data | heat efficiency (net, name plate) [] | ELH_0006 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.2335 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.2016 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.1378 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 1.0634 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 1.0102 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.86133 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.4462 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.4568 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.74436 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.72309 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.69119 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.65929 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.59549 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.52105 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.89323 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.89323 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.48915 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.47852 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.44662 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.40408 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.41472 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.34028 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.56359 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.56359 | biomass chp - back pressure - straw - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.09 | biomass chp - back pressure - straw - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.09 | biomass chp - back pressure - straw - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.09 | biomass chp - back pressure - straw - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.09 | biomass chp - back pressure - straw - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.09 | biomass chp - back pressure - straw - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.09 | biomass chp - back pressure - straw - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | steam reheat | ELH_0006 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | steam reheat | ELH_0006 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | steam reheat | ELH_0006 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | steam reheat | ELH_0006 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | steam reheat | ELH_0006 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | steam reheat | ELH_0006 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | steam reheat | ELH_0006 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 0 | biomass chp - back pressure - straw - medium | technology-specific data | steam reheat | ELH_0006 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.70183 | biomass chp - back pressure - straw - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.70183 | biomass chp - back pressure - straw - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.70183 | biomass chp - back pressure - straw - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.70183 | biomass chp - back pressure - straw - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232 | biomass chp - back pressure - straw - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.47852 | biomass chp - back pressure - straw - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.80816 | biomass chp - back pressure - straw - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.87197 | biomass chp - back pressure - straw - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0006 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.023732 | biomass chp - back pressure - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.023732 | biomass chp - back pressure - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.023741 | biomass chp - back pressure - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.023698 | biomass chp - back pressure - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.018068 | biomass chp - back pressure - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.014428 | biomass chp - back pressure - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.025941 | biomass chp - back pressure - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.025902 | biomass chp - back pressure - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.18 | biomass chp - back pressure - straw - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.18 | biomass chp - back pressure - straw - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.18 | biomass chp - back pressure - straw - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.18 | biomass chp - back pressure - straw - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.17 | biomass chp - back pressure - straw - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.17 | biomass chp - back pressure - straw - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.18 | biomass chp - back pressure - straw - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.18 | biomass chp - back pressure - straw - small | energy/technical data | cb coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0014
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1 | biomass chp - back pressure - straw - small | energy/technical data | construction time [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1 | biomass chp - back pressure - straw - small | energy/technical data | construction time [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1 | biomass chp - back pressure - straw - small | energy/technical data | construction time [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1 | biomass chp - back pressure - straw - small | energy/technical data | construction time [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5 | biomass chp - back pressure - straw - small | energy/technical data | construction time [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5 | biomass chp - back pressure - straw - small | energy/technical data | construction time [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5 | biomass chp - back pressure - straw - small | energy/technical data | construction time [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5 | biomass chp - back pressure - straw - small | energy/technical data | construction time [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1 | biomass chp - back pressure - straw - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1 | biomass chp - back pressure - straw - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1 | biomass chp - back pressure - straw - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1 | biomass chp - back pressure - straw - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1 | biomass chp - back pressure - straw - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1 | biomass chp - back pressure - straw - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1 | biomass chp - back pressure - straw - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1 | biomass chp - back pressure - straw - small | energy/technical data | cv coefficient (40°c/80°c) | ELH_0007 | tk_etd | manual_category_map | PAR_0027
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.14486 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.14486 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.14532 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.14304 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.13 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.13 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.15 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.15 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0034
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.15249 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.15249 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.15297 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.15057 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.14 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.14 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.16 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.16 | biomass chp - back pressure - straw - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0007 | tk_etd | manual_category_map | PAR_0036
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.04 | biomass chp - back pressure - straw - small | energy/technical data | forced outage [] | ELH_0007 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.04 | biomass chp - back pressure - straw - small | energy/technical data | forced outage [] | ELH_0007 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.04 | biomass chp - back pressure - straw - small | energy/technical data | forced outage [] | ELH_0007 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.04 | biomass chp - back pressure - straw - small | energy/technical data | forced outage [] | ELH_0007 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.04 | biomass chp - back pressure - straw - small | energy/technical data | forced outage [] | ELH_0007 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.04 | biomass chp - back pressure - straw - small | energy/technical data | forced outage [] | ELH_0007 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.04 | biomass chp - back pressure - straw - small | energy/technical data | forced outage [] | ELH_0007 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.04 | biomass chp - back pressure - straw - small | energy/technical data | forced outage [] | ELH_0007 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 3.05 | biomass chp - back pressure - straw - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 3.05 | biomass chp - back pressure - straw - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 3.06 | biomass chp - back pressure - straw - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 3.01 | biomass chp - back pressure - straw - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 2.97 | biomass chp - back pressure - straw - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 2.92 | biomass chp - back pressure - straw - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 3.09 | biomass chp - back pressure - straw - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 3.04 | biomass chp - back pressure - straw - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0071
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 4 | biomass chp - back pressure - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0007 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 4 | biomass chp - back pressure - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0007 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 4 | biomass chp - back pressure - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0007 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 4 | biomass chp - back pressure - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0007 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 3.4 | biomass chp - back pressure - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0007 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 3 | biomass chp - back pressure - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0007 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 4.6 | biomass chp - back pressure - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0007 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 5 | biomass chp - back pressure - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0007 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.98 | biomass chp - back pressure - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.98 | biomass chp - back pressure - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.98 | biomass chp - back pressure - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 1 | biomass chp - back pressure - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.84 | biomass chp - back pressure - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.75 | biomass chp - back pressure - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 1.13 | biomass chp - back pressure - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 1.25 | biomass chp - back pressure - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0007 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp - back pressure - straw - small | energy/technical data | technical lifetime [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp - back pressure - straw - small | energy/technical data | technical lifetime [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp - back pressure - straw - small | energy/technical data | technical lifetime [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp - back pressure - straw - small | energy/technical data | technical lifetime [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass chp - back pressure - straw - small | energy/technical data | technical lifetime [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass chp - back pressure - straw - small | energy/technical data | technical lifetime [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass chp - back pressure - straw - small | energy/technical data | technical lifetime [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass chp - back pressure - straw - small | energy/technical data | technical lifetime [years] | ELH_0007 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 16 | biomass chp - back pressure - straw - small | environment | ch4 [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 11 | biomass chp - back pressure - straw - small | environment | ch4 [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 8 | biomass chp - back pressure - straw - small | environment | ch4 [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 4 | biomass chp - back pressure - straw - small | environment | ch4 [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 4 | biomass chp - back pressure - straw - small | environment | ch4 [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 2 | biomass chp - back pressure - straw - small | environment | ch4 [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 16 | biomass chp - back pressure - straw - small | environment | ch4 [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 16 | biomass chp - back pressure - straw - small | environment | ch4 [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 1.2 | biomass chp - back pressure - straw - small | environment | n2o [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 1 | biomass chp - back pressure - straw - small | environment | n2o [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 1 | biomass chp - back pressure - straw - small | environment | n2o [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 1 | biomass chp - back pressure - straw - small | environment | n2o [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 1 | biomass chp - back pressure - straw - small | environment | n2o [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0 | biomass chp - back pressure - straw - small | environment | n2o [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 3 | biomass chp - back pressure - straw - small | environment | n2o [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 1 | biomass chp - back pressure - straw - small | environment | n2o [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 90 | biomass chp - back pressure - straw - small | environment | nox [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 70 | biomass chp - back pressure - straw - small | environment | nox [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 50 | biomass chp - back pressure - straw - small | environment | nox [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 40 | biomass chp - back pressure - straw - small | environment | nox [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 50 | biomass chp - back pressure - straw - small | environment | nox [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 40 | biomass chp - back pressure - straw - small | environment | nox [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 90 | biomass chp - back pressure - straw - small | environment | nox [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 50 | biomass chp - back pressure - straw - small | environment | nox [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 2 | biomass chp - back pressure - straw - small | environment | particles [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 0.3 | biomass chp - back pressure - straw - small | environment | particles [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 0.3 | biomass chp - back pressure - straw - small | environment | particles [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 0.3 | biomass chp - back pressure - straw - small | environment | particles [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 0.1 | biomass chp - back pressure - straw - small | environment | particles [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0.1 | biomass chp - back pressure - straw - small | environment | particles [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 2 | biomass chp - back pressure - straw - small | environment | particles [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 1 | biomass chp - back pressure - straw - small | environment | particles [g/gj_i] | ELH_0007 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2015 | 0.9545 | biomass chp - back pressure - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0007 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2020 | 0.9636 | biomass chp - back pressure - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0007 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2030 | 0.9909 | biomass chp - back pressure - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0007 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2050 | 0.99818 | biomass chp - back pressure - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0007 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | lower | 2020 | 0.909 | biomass chp - back pressure - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0007 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | lower | 2050 | 0.9545 | biomass chp - back pressure - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0007 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | upper | 2020 | 0.99818 | biomass chp - back pressure - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0007 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | upper | 2050 | 0.99909 | biomass chp - back pressure - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0007 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2015 | 338152.5243 | biomass chp - back pressure - straw - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0007 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2020 | 332835.6607 | biomass chp - back pressure - straw - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0007 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2030 | 321138.5608 | biomass chp - back pressure - straw - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0007 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2050 | 311568.2064 | biomass chp - back pressure - straw - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0007 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2020 | 284983.8884 | biomass chp - back pressure - straw - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0007 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2050 | 241385.607 | biomass chp - back pressure - straw - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0007 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2020 | 384940.9239 | biomass chp - back pressure - straw - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0007 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2050 | 398764.7693 | biomass chp - back pressure - straw - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0007 | tk_fin | manual_category_map | PAR_0042
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2015 | 7.2841 | biomass chp - back pressure - straw - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2020 | 7.1033 | biomass chp - back pressure - straw - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2030 | 6.7418 | biomass chp - back pressure - straw - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2050 | 6.4759 | biomass chp - back pressure - straw - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2020 | 6.1995 | biomass chp - back pressure - straw - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2050 | 5.4126 | biomass chp - back pressure - straw - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2020 | 8.3794 | biomass chp - back pressure - straw - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2050 | 8.8366 | biomass chp - back pressure - straw - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0093
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 4.1153 | biomass chp - back pressure - straw - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 4.0089 | biomass chp - back pressure - straw - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 3.8069 | biomass chp - back pressure - straw - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 3.775 | biomass chp - back pressure - straw - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 3.4985 | biomass chp - back pressure - straw - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 3.1795 | biomass chp - back pressure - straw - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 4.732 | biomass chp - back pressure - straw - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 5.1148 | biomass chp - back pressure - straw - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0104
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 3.1689 | biomass chp - back pressure - straw - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 3.0944 | biomass chp - back pressure - straw - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.9349 | biomass chp - back pressure - straw - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.701 | biomass chp - back pressure - straw - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 2.701 | biomass chp - back pressure - straw - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 2.2331 | biomass chp - back pressure - straw - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 3.6474 | biomass chp - back pressure - straw - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 3.7218 | biomass chp - back pressure - straw - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0115
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.8064 | biomass chp - back pressure - straw - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.8064 | biomass chp - back pressure - straw - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.7852 | biomass chp - back pressure - straw - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.8596 | biomass chp - back pressure - straw - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.5517 | biomass chp - back pressure - straw - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 3.1795 | biomass chp - back pressure - straw - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 5.4445 | biomass chp - back pressure - straw - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 5.9336 | biomass chp - back pressure - straw - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0007 | tk_fin | manual_category_map | PAR_0201
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | cold start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | cold start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | cold start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | cold start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | cold start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | cold start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | cold start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | cold start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2015 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | minimum load (of full load) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2020 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | minimum load (of full load) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2030 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | minimum load (of full load) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2050 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | minimum load (of full load) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2020 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | minimum load (of full load) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2050 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | minimum load (of full load) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2020 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | minimum load (of full load) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2050 | 0.5 | biomass chp - back pressure - straw - small | regulation ability | minimum load (of full load) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.1 | biomass chp - back pressure - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.1 | biomass chp - back pressure - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.1 | biomass chp - back pressure - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.1 | biomass chp - back pressure - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.1 | biomass chp - back pressure - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.1 | biomass chp - back pressure - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.1 | biomass chp - back pressure - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.1 | biomass chp - back pressure - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0007 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 0.25 | biomass chp - back pressure - straw - small | regulation ability | warm start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 0.25 | biomass chp - back pressure - straw - small | regulation ability | warm start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 0.25 | biomass chp - back pressure - straw - small | regulation ability | warm start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 0.25 | biomass chp - back pressure - straw - small | regulation ability | warm start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 0.25 | biomass chp - back pressure - straw - small | regulation ability | warm start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 0.25 | biomass chp - back pressure - straw - small | regulation ability | warm start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 0.25 | biomass chp - back pressure - straw - small | regulation ability | warm start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 0.25 | biomass chp - back pressure - straw - small | regulation ability | warm start-up time [hours] | ELH_0007 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.017669 | biomass chp - back pressure - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.017669 | biomass chp - back pressure - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017667 | biomass chp - back pressure - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017677 | biomass chp - back pressure - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01 | biomass chp - back pressure - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01 | biomass chp - back pressure - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.14 | biomass chp - back pressure - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.15 | biomass chp - back pressure - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - straw - small | technology-specific data | combustion air humidification | ELH_0007 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - straw - small | technology-specific data | combustion air humidification | ELH_0007 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - straw - small | technology-specific data | combustion air humidification | ELH_0007 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - straw - small | technology-specific data | combustion air humidification | ELH_0007 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - straw - small | technology-specific data | combustion air humidification | ELH_0007 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - straw - small | technology-specific data | combustion air humidification | ELH_0007 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - straw - small | technology-specific data | combustion air humidification | ELH_0007 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - straw - small | technology-specific data | combustion air humidification | ELH_0007 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2015 | 51679.9141 | biomass chp - back pressure - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0007 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2020 | 50722.8786 | biomass chp - back pressure - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0007 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2030 | 49021.4823 | biomass chp - back pressure - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0007 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2050 | 46894.7368 | biomass chp - back pressure - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0007 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2020 | 43385.6069 | biomass chp - back pressure - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0007 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2050 | 36367.3469 | biomass chp - back pressure - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0007 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2020 | 58804.5113 | biomass chp - back pressure - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0007 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2050 | 60080.5585 | biomass chp - back pressure - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0007 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1 | biomass chp - back pressure - straw - small | technology-specific data | flue gas condensation | ELH_0007 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1 | biomass chp - back pressure - straw - small | technology-specific data | flue gas condensation | ELH_0007 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1 | biomass chp - back pressure - straw - small | technology-specific data | flue gas condensation | ELH_0007 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1 | biomass chp - back pressure - straw - small | technology-specific data | flue gas condensation | ELH_0007 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0 | biomass chp - back pressure - straw - small | technology-specific data | flue gas condensation | ELH_0007 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0 | biomass chp - back pressure - straw - small | technology-specific data | flue gas condensation | ELH_0007 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1 | biomass chp - back pressure - straw - small | technology-specific data | flue gas condensation | ELH_0007 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1 | biomass chp - back pressure - straw - small | technology-specific data | flue gas condensation | ELH_0007 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.08507 | biomass chp - back pressure - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0007 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.08507 | biomass chp - back pressure - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0007 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.074436 | biomass chp - back pressure - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0007 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.074436 | biomass chp - back pressure - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0007 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.074436 | biomass chp - back pressure - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0007 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.063802 | biomass chp - back pressure - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0007 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.095704 | biomass chp - back pressure - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0007 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.095704 | biomass chp - back pressure - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0007 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.86339 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.86339 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.86291 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.86529 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.73 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.72 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.88 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.88 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, annual average) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0076
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.85576 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.85576 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.85526 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.85776 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.72 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.71 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.87 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.87 | biomass chp - back pressure - straw - small | technology-specific data | heat efficiency (net, name plate) [] | ELH_0007 | tk_tsd | manual_category_map | PAR_0077
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2015 | 1.1059 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2020 | 1.0846 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2030 | 1.0315 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2050 | 0.9783 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | lower | 2020 | 0.9464 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | lower | 2050 | 0.8188 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | upper | 2020 | 1.276 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | upper | 2050 | 1.3292 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.62739 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.61676 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.58485 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.56359 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.53169 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.47852 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.72309 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.76563 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.48915 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.46788 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.44662 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.40408 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.41472 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.34028 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.55295 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.56359 | biomass chp - back pressure - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.09 | biomass chp - back pressure - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.09 | biomass chp - back pressure - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.09 | biomass chp - back pressure - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.09 | biomass chp - back pressure - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0 | biomass chp - back pressure - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0 | biomass chp - back pressure - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.09 | biomass chp - back pressure - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.09 | biomass chp - back pressure - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0 | biomass chp - back pressure - straw - small | technology-specific data | steam reheat | ELH_0007 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0 | biomass chp - back pressure - straw - small | technology-specific data | steam reheat | ELH_0007 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0 | biomass chp - back pressure - straw - small | technology-specific data | steam reheat | ELH_0007 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0 | biomass chp - back pressure - straw - small | technology-specific data | steam reheat | ELH_0007 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0 | biomass chp - back pressure - straw - small | technology-specific data | steam reheat | ELH_0007 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0 | biomass chp - back pressure - straw - small | technology-specific data | steam reheat | ELH_0007 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 0 | biomass chp - back pressure - straw - small | technology-specific data | steam reheat | ELH_0007 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 0 | biomass chp - back pressure - straw - small | technology-specific data | steam reheat | ELH_0007 | tk_tsd | manual_category_map | PAR_0197
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.73373 | biomass chp - back pressure - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.73373 | biomass chp - back pressure - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.73373 | biomass chp - back pressure - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.73373 | biomass chp - back pressure - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232 | biomass chp - back pressure - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.47852 | biomass chp - back pressure - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.82943 | biomass chp - back pressure - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.89323 | biomass chp - back pressure - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0007 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2015 | 0.022162 | biomass boiler - boiler - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2020 | 0.022162 | biomass boiler - boiler - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2030 | 0.022162 | biomass boiler - boiler - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2050 | 0.022162 | biomass boiler - boiler - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2020 | 0.021135 | biomass boiler - boiler - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2050 | 0.01691 | biomass boiler - boiler - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2020 | 0.024723 | biomass boiler - boiler - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2050 | 0.024702 | biomass boiler - boiler - wood chips - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - small | energy/technical data | construction time [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - small | energy/technical data | construction time [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - small | energy/technical data | construction time [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - small | energy/technical data | construction time [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5 | biomass boiler - boiler - wood chips - small | energy/technical data | construction time [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5 | biomass boiler - boiler - wood chips - small | energy/technical data | construction time [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5 | biomass boiler - boiler - wood chips - small | energy/technical data | construction time [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5 | biomass boiler - boiler - wood chips - small | energy/technical data | construction time [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass boiler - boiler - wood chips - small | energy/technical data | forced outage [] | ELH_0004 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass boiler - boiler - wood chips - small | energy/technical data | forced outage [] | ELH_0004 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass boiler - boiler - wood chips - small | energy/technical data | forced outage [] | ELH_0004 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass boiler - boiler - wood chips - small | energy/technical data | forced outage [] | ELH_0004 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass boiler - boiler - wood chips - small | energy/technical data | forced outage [] | ELH_0004 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass boiler - boiler - wood chips - small | energy/technical data | forced outage [] | ELH_0004 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass boiler - boiler - wood chips - small | energy/technical data | forced outage [] | ELH_0004 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass boiler - boiler - wood chips - small | energy/technical data | forced outage [] | ELH_0004 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 6.84 | biomass boiler - boiler - wood chips - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 6.84 | biomass boiler - boiler - wood chips - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 6.84 | biomass boiler - boiler - wood chips - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 6.84 | biomass boiler - boiler - wood chips - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 5.34 | biomass boiler - boiler - wood chips - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 5.34 | biomass boiler - boiler - wood chips - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 6.86 | biomass boiler - boiler - wood chips - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 6.87 | biomass boiler - boiler - wood chips - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1401 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1401 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1401 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1401 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.89 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.15 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.15 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1401 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1401 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1401 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1401 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.89 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.15 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.15 | biomass boiler - boiler - wood chips - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0004 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0004 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 2 | biomass boiler - boiler - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0004 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 2 | biomass boiler - boiler - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0004 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 2 | biomass boiler - boiler - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0004 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 1.7 | biomass boiler - boiler - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0004 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 1.5 | biomass boiler - boiler - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0004 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 2.3 | biomass boiler - boiler - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0004 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 2.5 | biomass boiler - boiler - wood chips - small | energy/technical data | planned outage [weeks per year] | ELH_0004 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.22 | biomass boiler - boiler - wood chips - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.22 | biomass boiler - boiler - wood chips - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0.22 | biomass boiler - boiler - wood chips - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0.22 | biomass boiler - boiler - wood chips - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0.19 | biomass boiler - boiler - wood chips - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0.16 | biomass boiler - boiler - wood chips - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.25 | biomass boiler - boiler - wood chips - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.27 | biomass boiler - boiler - wood chips - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0004 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass boiler - boiler - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass boiler - boiler - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass boiler - boiler - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass boiler - boiler - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass boiler - boiler - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass boiler - boiler - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass boiler - boiler - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass boiler - boiler - wood chips - small | energy/technical data | technical lifetime [years] | ELH_0004 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 16 | biomass boiler - boiler - wood chips - small | environment | ch4 [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 11 | biomass boiler - boiler - wood chips - small | environment | ch4 [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 8 | biomass boiler - boiler - wood chips - small | environment | ch4 [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 4 | biomass boiler - boiler - wood chips - small | environment | ch4 [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 4 | biomass boiler - boiler - wood chips - small | environment | ch4 [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 2 | biomass boiler - boiler - wood chips - small | environment | ch4 [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 16 | biomass boiler - boiler - wood chips - small | environment | ch4 [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 16 | biomass boiler - boiler - wood chips - small | environment | ch4 [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 4 | biomass boiler - boiler - wood chips - small | environment | n2o [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 3 | biomass boiler - boiler - wood chips - small | environment | n2o [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 3 | biomass boiler - boiler - wood chips - small | environment | n2o [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - small | environment | n2o [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 1 | biomass boiler - boiler - wood chips - small | environment | n2o [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 1 | biomass boiler - boiler - wood chips - small | environment | n2o [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 4 | biomass boiler - boiler - wood chips - small | environment | n2o [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 4 | biomass boiler - boiler - wood chips - small | environment | n2o [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 90 | biomass boiler - boiler - wood chips - small | environment | nox [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 60 | biomass boiler - boiler - wood chips - small | environment | nox [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 50 | biomass boiler - boiler - wood chips - small | environment | nox [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 40 | biomass boiler - boiler - wood chips - small | environment | nox [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 40 | biomass boiler - boiler - wood chips - small | environment | nox [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 30 | biomass boiler - boiler - wood chips - small | environment | nox [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 80 | biomass boiler - boiler - wood chips - small | environment | nox [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 40 | biomass boiler - boiler - wood chips - small | environment | nox [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - small | environment | particles [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 0.3 | biomass boiler - boiler - wood chips - small | environment | particles [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 0.3 | biomass boiler - boiler - wood chips - small | environment | particles [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 0.3 | biomass boiler - boiler - wood chips - small | environment | particles [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 0.1 | biomass boiler - boiler - wood chips - small | environment | particles [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 0.1 | biomass boiler - boiler - wood chips - small | environment | particles [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 2 | biomass boiler - boiler - wood chips - small | environment | particles [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 1 | biomass boiler - boiler - wood chips - small | environment | particles [g/gj_i] | ELH_0004 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9797 | biomass boiler - boiler - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0004 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9797 | biomass boiler - boiler - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0004 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9797 | biomass boiler - boiler - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0004 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.9797 | biomass boiler - boiler - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0004 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.8985 | biomass boiler - boiler - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0004 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9797 | biomass boiler - boiler - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0004 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.98985 | biomass boiler - boiler - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0004 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.98985 | biomass boiler - boiler - wood chips - small | environment | so2 (degree of desulphuring) [] | ELH_0004 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2015 | 35091.2997 | biomass boiler - boiler - wood chips - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0004 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2020 | 34559.6133 | biomass boiler - boiler - wood chips - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0004 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2030 | 33496.2406 | biomass boiler - boiler - wood chips - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0004 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2050 | 31475.8325 | biomass boiler - boiler - wood chips - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0004 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2020 | 29561.7616 | biomass boiler - boiler - wood chips - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0004 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2050 | 24244.898 | biomass boiler - boiler - wood chips - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0004 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2020 | 40089.1515 | biomass boiler - boiler - wood chips - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0004 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2050 | 40408.1633 | biomass boiler - boiler - wood chips - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0004 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.75499 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.73373 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.70183 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.62739 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.63802 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.52105 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.86133 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.87197 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.43598 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.42535 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.40408 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.36155 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.37218 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.29774 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.49979 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.49979 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.31901 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.30838 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.29774 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.26584 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.26584 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.22331 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.36155 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.37218 | biomass boiler - boiler - wood chips - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 2.7541 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 2.8924 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 3.6474 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 4.0195 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 2.4883 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 3.4985 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 3.9451 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 5.5508 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.4887 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.627 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 2.382 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 2.7541 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 1.6057 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 2.7222 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 2.1161 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 3.5942 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.2654 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.2654 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 1.2654 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 1.2654 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 0.8826 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0.77626 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 1.829 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 1.9566 | biomass boiler - boiler - wood chips - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0004 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5 | biomass boiler - boiler - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5 | biomass boiler - boiler - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5 | biomass boiler - boiler - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5 | biomass boiler - boiler - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5 | biomass boiler - boiler - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5 | biomass boiler - boiler - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5 | biomass boiler - boiler - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5 | biomass boiler - boiler - wood chips - small | regulation ability | cold start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2015 | 0.2 | biomass boiler - boiler - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2020 | 0.2 | biomass boiler - boiler - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2030 | 0.2 | biomass boiler - boiler - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2050 | 0.2 | biomass boiler - boiler - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2020 | 0.2 | biomass boiler - boiler - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2050 | 0.2 | biomass boiler - boiler - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2020 | 0.2 | biomass boiler - boiler - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2050 | 0.2 | biomass boiler - boiler - wood chips - small | regulation ability | minimum load (of full load) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1 | biomass boiler - boiler - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1 | biomass boiler - boiler - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1 | biomass boiler - boiler - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1 | biomass boiler - boiler - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1 | biomass boiler - boiler - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1 | biomass boiler - boiler - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1 | biomass boiler - boiler - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1 | biomass boiler - boiler - wood chips - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0004 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 0.25 | biomass boiler - boiler - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 0.25 | biomass boiler - boiler - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 0.25 | biomass boiler - boiler - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 0.25 | biomass boiler - boiler - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 0.25 | biomass boiler - boiler - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 0.25 | biomass boiler - boiler - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 0.25 | biomass boiler - boiler - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 0.25 | biomass boiler - boiler - wood chips - small | regulation ability | warm start-up time [hours] | ELH_0004 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.019432 | biomass boiler - boiler - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0004 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.019432 | biomass boiler - boiler - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0004 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.019432 | biomass boiler - boiler - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0004 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.019432 | biomass boiler - boiler - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0004 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01 | biomass boiler - boiler - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0004 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01 | biomass boiler - boiler - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0004 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.26 | biomass boiler - boiler - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0004 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.26 | biomass boiler - boiler - wood chips - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0004 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | combustion air humidification | ELH_0004 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | combustion air humidification | ELH_0004 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | combustion air humidification | ELH_0004 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | combustion air humidification | ELH_0004 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - small | technology-specific data | combustion air humidification | ELH_0004 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - small | technology-specific data | combustion air humidification | ELH_0004 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2020 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | combustion air humidification | ELH_0004 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2050 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | combustion air humidification | ELH_0004 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 40089.1515 | biomass boiler - boiler - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0004 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 39451.1278 | biomass boiler - boiler - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0004 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 38175.0806 | biomass boiler - boiler - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0004 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 35835.6606 | biomass boiler - boiler - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0004 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 33708.9151 | biomass boiler - boiler - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0004 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 27647.6907 | biomass boiler - boiler - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0004 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 45618.6896 | biomass boiler - boiler - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0004 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 46044.0387 | biomass boiler - boiler - wood chips - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0004 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | flue gas condensation | ELH_0004 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | flue gas condensation | ELH_0004 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | flue gas condensation | ELH_0004 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | flue gas condensation | ELH_0004 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - small | technology-specific data | flue gas condensation | ELH_0004 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - small | technology-specific data | flue gas condensation | ELH_0004 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2020 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | flue gas condensation | ELH_0004 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2050 | 1 | biomass boiler - boiler - wood chips - small | technology-specific data | flue gas condensation | ELH_0004 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2015 | 0.021267 | biomass boiler - boiler - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0004 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2020 | 0.021267 | biomass boiler - boiler - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0004 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2030 | 0.021267 | biomass boiler - boiler - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0004 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2050 | 0.021267 | biomass boiler - boiler - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0004 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2020 | 0.021267 | biomass boiler - boiler - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0004 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2050 | 0.010634 | biomass boiler - boiler - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0004 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2020 | 0.021267 | biomass boiler - boiler - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0004 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2050 | 0.021267 | biomass boiler - boiler - wood chips - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0004 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2015 | 0.86133 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2020 | 0.84006 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2030 | 0.79753 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2050 | 0.72309 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | lower | 2020 | 0.73373 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | lower | 2050 | 0.59549 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | upper | 2020 | 0.98894 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | upper | 2050 | 0.99957 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.49979 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.48915 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.45725 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.41472 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.42535 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.34028 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.57422 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.57422 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.36155 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.35091 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.34028 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.30838 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.30838 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.25521 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.41472 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.41472 | biomass boiler - boiler - wood chips - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2015 | 0.25 | biomass boiler - boiler - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2020 | 0.25 | biomass boiler - boiler - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2030 | 0.25 | biomass boiler - boiler - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2050 | 0.25 | biomass boiler - boiler - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2020 | 0.25 | biomass boiler - boiler - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2050 | 0.25 | biomass boiler - boiler - wood chips - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2015 | 3.1369 | biomass boiler - boiler - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2020 | 3.2965 | biomass boiler - boiler - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2030 | 4.1578 | biomass boiler - boiler - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2050 | 4.5831 | biomass boiler - boiler - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2020 | 2.8498 | biomass boiler - boiler - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2050 | 4.0089 | biomass boiler - boiler - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2020 | 3.5091 | biomass boiler - boiler - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2050 | 4.9447 | biomass boiler - boiler - wood chips - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0004 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2015 | 0.022039 | biomass boiler - boiler - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2020 | 0.022039 | biomass boiler - boiler - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2030 | 0.022039 | biomass boiler - boiler - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2050 | 0.022026 | biomass boiler - boiler - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2020 | 0.02098 | biomass boiler - boiler - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2050 | 0.017093 | biomass boiler - boiler - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2020 | 0.024587 | biomass boiler - boiler - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2050 | 0.024549 | biomass boiler - boiler - wood chips - medium | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - medium | energy/technical data | construction time [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2 | biomass boiler - boiler - wood chips - medium | energy/technical data | construction time [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2 | biomass boiler - boiler - wood chips - medium | energy/technical data | construction time [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2 | biomass boiler - boiler - wood chips - medium | energy/technical data | construction time [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 1.5 | biomass boiler - boiler - wood chips - medium | energy/technical data | construction time [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5 | biomass boiler - boiler - wood chips - medium | energy/technical data | construction time [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 2.5 | biomass boiler - boiler - wood chips - medium | energy/technical data | construction time [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 2.5 | biomass boiler - boiler - wood chips - medium | energy/technical data | construction time [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass boiler - boiler - wood chips - medium | energy/technical data | forced outage [] | ELH_0003 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass boiler - boiler - wood chips - medium | energy/technical data | forced outage [] | ELH_0003 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass boiler - boiler - wood chips - medium | energy/technical data | forced outage [] | ELH_0003 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass boiler - boiler - wood chips - medium | energy/technical data | forced outage [] | ELH_0003 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass boiler - boiler - wood chips - medium | energy/technical data | forced outage [] | ELH_0003 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass boiler - boiler - wood chips - medium | energy/technical data | forced outage [] | ELH_0003 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass boiler - boiler - wood chips - medium | energy/technical data | forced outage [] | ELH_0003 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass boiler - boiler - wood chips - medium | energy/technical data | forced outage [] | ELH_0003 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 51.64 | biomass boiler - boiler - wood chips - medium | energy/technical data | generating capacity for one unit [mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 51.64 | biomass boiler - boiler - wood chips - medium | energy/technical data | generating capacity for one unit [mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 51.64 | biomass boiler - boiler - wood chips - medium | energy/technical data | generating capacity for one unit [mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 51.64 | biomass boiler - boiler - wood chips - medium | energy/technical data | generating capacity for one unit [mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 40.38 | biomass boiler - boiler - wood chips - medium | energy/technical data | generating capacity for one unit [mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 39.66 | biomass boiler - boiler - wood chips - medium | energy/technical data | generating capacity for one unit [mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 51.81 | biomass boiler - boiler - wood chips - medium | energy/technical data | generating capacity for one unit [mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 51.86 | biomass boiler - boiler - wood chips - medium | energy/technical data | generating capacity for one unit [mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1475 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, annual average) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1475 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, annual average) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1475 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, annual average) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1475 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, annual average) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, annual average) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, annual average) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.16 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, annual average) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.16 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, annual average) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1475 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, name plate) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1475 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, name plate) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1475 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, name plate) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1475 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, name plate) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, name plate) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, name plate) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.16 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, name plate) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.16 | biomass boiler - boiler - wood chips - medium | energy/technical data | heat efficiency (net, name plate) [] | ELH_0003 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0003 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 2 | biomass boiler - boiler - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0003 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 2 | biomass boiler - boiler - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0003 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 2 | biomass boiler - boiler - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0003 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 1.7 | biomass boiler - boiler - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0003 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 1.5 | biomass boiler - boiler - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0003 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 2.3 | biomass boiler - boiler - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0003 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 2.5 | biomass boiler - boiler - wood chips - medium | energy/technical data | planned outage [weeks per year] | ELH_0003 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.06 | biomass boiler - boiler - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.06 | biomass boiler - boiler - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0.06 | biomass boiler - boiler - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0.06 | biomass boiler - boiler - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0.05 | biomass boiler - boiler - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0.04 | biomass boiler - boiler - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.07 | biomass boiler - boiler - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.07 | biomass boiler - boiler - wood chips - medium | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0003 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass boiler - boiler - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass boiler - boiler - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass boiler - boiler - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass boiler - boiler - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass boiler - boiler - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass boiler - boiler - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass boiler - boiler - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass boiler - boiler - wood chips - medium | energy/technical data | technical lifetime [years] | ELH_0003 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 16 | biomass boiler - boiler - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 11 | biomass boiler - boiler - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 8 | biomass boiler - boiler - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 4 | biomass boiler - boiler - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 4 | biomass boiler - boiler - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 2 | biomass boiler - boiler - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 16 | biomass boiler - boiler - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 16 | biomass boiler - boiler - wood chips - medium | environment | ch4 [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - medium | environment | n2o [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - medium | environment | n2o [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - medium | environment | n2o [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 0 | biomass boiler - boiler - wood chips - medium | environment | n2o [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 0 | biomass boiler - boiler - wood chips - medium | environment | n2o [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 0 | biomass boiler - boiler - wood chips - medium | environment | n2o [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 1 | biomass boiler - boiler - wood chips - medium | environment | n2o [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 1 | biomass boiler - boiler - wood chips - medium | environment | n2o [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 90 | biomass boiler - boiler - wood chips - medium | environment | nox [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 60 | biomass boiler - boiler - wood chips - medium | environment | nox [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 40 | biomass boiler - boiler - wood chips - medium | environment | nox [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 30 | biomass boiler - boiler - wood chips - medium | environment | nox [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 40 | biomass boiler - boiler - wood chips - medium | environment | nox [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 20 | biomass boiler - boiler - wood chips - medium | environment | nox [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 80 | biomass boiler - boiler - wood chips - medium | environment | nox [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 40 | biomass boiler - boiler - wood chips - medium | environment | nox [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - medium | environment | particles [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 0.3 | biomass boiler - boiler - wood chips - medium | environment | particles [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 0.3 | biomass boiler - boiler - wood chips - medium | environment | particles [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 0.3 | biomass boiler - boiler - wood chips - medium | environment | particles [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 0.1 | biomass boiler - boiler - wood chips - medium | environment | particles [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 0.1 | biomass boiler - boiler - wood chips - medium | environment | particles [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 2 | biomass boiler - boiler - wood chips - medium | environment | particles [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 1 | biomass boiler - boiler - wood chips - medium | environment | particles [g/gj_i] | ELH_0003 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9797 | biomass boiler - boiler - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0003 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9797 | biomass boiler - boiler - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0003 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9797 | biomass boiler - boiler - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0003 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.9797 | biomass boiler - boiler - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0003 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.94925 | biomass boiler - boiler - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0003 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9797 | biomass boiler - boiler - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0003 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.98985 | biomass boiler - boiler - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0003 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.98985 | biomass boiler - boiler - wood chips - medium | environment | so2 (degree of desulphuring) [] | ELH_0003 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2015 | 45512.3523 | biomass boiler - boiler - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0003 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2020 | 44661.6542 | biomass boiler - boiler - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0003 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2030 | 43066.5951 | biomass boiler - boiler - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0003 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2050 | 40620.8378 | biomass boiler - boiler - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0003 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2020 | 38068.7433 | biomass boiler - boiler - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0003 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2050 | 30625.1343 | biomass boiler - boiler - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0003 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2020 | 51573.5768 | biomass boiler - boiler - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0003 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2050 | 51573.5768 | biomass boiler - boiler - wood chips - medium | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0003 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.54232 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (*total) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.52105 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (*total) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.49979 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (*total) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.47852 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (*total) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.45725 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (*total) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.37218 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (*total) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.61676 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (*total) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.65929 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (*total) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.39345 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.38281 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.36155 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.36155 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.32965 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.27648 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.45725 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.48915 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.14887 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (installation) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.13824 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (installation) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.13824 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (installation) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.11697 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (installation) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.1276 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (installation) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.095704 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (installation) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.17014 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (installation) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.17014 | biomass boiler - boiler - wood chips - medium | financial data | nominal investment (installation) [meur/mw_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 2.7329 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 2.8711 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 3.6261 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 3.9983 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 2.4777 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 3.4772 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 3.9132 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 5.604 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.4781 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.6163 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 2.3713 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 2.7435 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 1.5951 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 2.7116 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 2.1055 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 3.6261 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.2548 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.2548 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 1.2548 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 1.2548 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 0.87197 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0.76563 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 1.8077 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 1.9779 | biomass boiler - boiler - wood chips - medium | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0003 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8 | biomass boiler - boiler - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8 | biomass boiler - boiler - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8 | biomass boiler - boiler - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8 | biomass boiler - boiler - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8 | biomass boiler - boiler - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8 | biomass boiler - boiler - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8 | biomass boiler - boiler - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8 | biomass boiler - boiler - wood chips - medium | regulation ability | cold start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.4 | biomass boiler - boiler - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.4 | biomass boiler - boiler - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.4 | biomass boiler - boiler - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.4 | biomass boiler - boiler - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.4 | biomass boiler - boiler - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.4 | biomass boiler - boiler - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.4 | biomass boiler - boiler - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.4 | biomass boiler - boiler - wood chips - medium | regulation ability | minimum load (of full load) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1 | biomass boiler - boiler - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1 | biomass boiler - boiler - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1 | biomass boiler - boiler - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1 | biomass boiler - boiler - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1 | biomass boiler - boiler - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1 | biomass boiler - boiler - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1 | biomass boiler - boiler - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1 | biomass boiler - boiler - wood chips - medium | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0003 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 2 | biomass boiler - boiler - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 2 | biomass boiler - boiler - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 2 | biomass boiler - boiler - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 2 | biomass boiler - boiler - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 2 | biomass boiler - boiler - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 2 | biomass boiler - boiler - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 2 | biomass boiler - boiler - wood chips - medium | regulation ability | warm start-up time [hours] | ELH_0003 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.019432 | biomass boiler - boiler - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0003 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.019432 | biomass boiler - boiler - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0003 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.019432 | biomass boiler - boiler - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0003 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.019442 | biomass boiler - boiler - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0003 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01 | biomass boiler - boiler - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0003 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01 | biomass boiler - boiler - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0003 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.26 | biomass boiler - boiler - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0003 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.28 | biomass boiler - boiler - wood chips - medium | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0003 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | combustion air humidification | ELH_0003 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | combustion air humidification | ELH_0003 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | combustion air humidification | ELH_0003 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | combustion air humidification | ELH_0003 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - medium | technology-specific data | combustion air humidification | ELH_0003 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - medium | technology-specific data | combustion air humidification | ELH_0003 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2020 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | combustion air humidification | ELH_0003 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2050 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | combustion air humidification | ELH_0003 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 52211.6004 | biomass boiler - boiler - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0003 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 51254.565 | biomass boiler - boiler - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0003 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 49340.4941 | biomass boiler - boiler - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0003 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 46682.0623 | biomass boiler - boiler - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0003 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 43704.6187 | biomass boiler - boiler - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0003 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 35091.2997 | biomass boiler - boiler - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0003 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 59123.5231 | biomass boiler - boiler - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0003 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 59229.8604 | biomass boiler - boiler - wood chips - medium | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0003 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | flue gas condensation | ELH_0003 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | flue gas condensation | ELH_0003 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | flue gas condensation | ELH_0003 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | flue gas condensation | ELH_0003 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - medium | technology-specific data | flue gas condensation | ELH_0003 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - medium | technology-specific data | flue gas condensation | ELH_0003 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2020 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | flue gas condensation | ELH_0003 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2050 | 1 | biomass boiler - boiler - wood chips - medium | technology-specific data | flue gas condensation | ELH_0003 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2015 | 0.021267 | biomass boiler - boiler - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0003 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2020 | 0.021267 | biomass boiler - boiler - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0003 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2030 | 0.021267 | biomass boiler - boiler - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0003 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2050 | 0.010634 | biomass boiler - boiler - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0003 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2020 | 0.010634 | biomass boiler - boiler - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0003 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2050 | 0.010634 | biomass boiler - boiler - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0003 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2020 | 0.021267 | biomass boiler - boiler - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0003 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2050 | 0.021267 | biomass boiler - boiler - wood chips - medium | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0003 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2015 | 0.61676 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2020 | 0.60612 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2030 | 0.57422 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2050 | 0.55295 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | lower | 2020 | 0.52105 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | lower | 2050 | 0.42535 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | upper | 2020 | 0.71246 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | upper | 2050 | 0.75499 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.44662 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.43598 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.41472 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.41472 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.38281 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.31901 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.52105 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.56359 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.17014 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.15951 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.14887 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.13824 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.13824 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.11697 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.19141 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.19141 | biomass boiler - boiler - wood chips - medium | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2015 | 0.25 | biomass boiler - boiler - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2020 | 0.25 | biomass boiler - boiler - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2030 | 0.25 | biomass boiler - boiler - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2050 | 0.25 | biomass boiler - boiler - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2020 | 0.25 | biomass boiler - boiler - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2050 | 0.25 | biomass boiler - boiler - wood chips - medium | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2015 | 3.1369 | biomass boiler - boiler - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2020 | 3.2965 | biomass boiler - boiler - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2030 | 4.1578 | biomass boiler - boiler - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2050 | 4.5938 | biomass boiler - boiler - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2020 | 2.8498 | biomass boiler - boiler - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2050 | 4.0089 | biomass boiler - boiler - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2020 | 3.5091 | biomass boiler - boiler - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2050 | 4.9447 | biomass boiler - boiler - wood chips - medium | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0003 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2015 | 0.022012 | biomass boiler - boiler - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2020 | 0.022012 | biomass boiler - boiler - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2030 | 0.022012 | biomass boiler - boiler - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2050 | 0.021998 | biomass boiler - boiler - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2020 | 0.020946 | biomass boiler - boiler - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2050 | 0.017064 | biomass boiler - boiler - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2020 | 0.024556 | biomass boiler - boiler - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2050 | 0.024519 | biomass boiler - boiler - wood chips - large | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0005
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5 | biomass boiler - boiler - wood chips - large | energy/technical data | construction time [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5 | biomass boiler - boiler - wood chips - large | energy/technical data | construction time [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5 | biomass boiler - boiler - wood chips - large | energy/technical data | construction time [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5 | biomass boiler - boiler - wood chips - large | energy/technical data | construction time [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2 | biomass boiler - boiler - wood chips - large | energy/technical data | construction time [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2 | biomass boiler - boiler - wood chips - large | energy/technical data | construction time [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3 | biomass boiler - boiler - wood chips - large | energy/technical data | construction time [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3 | biomass boiler - boiler - wood chips - large | energy/technical data | construction time [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass boiler - boiler - wood chips - large | energy/technical data | forced outage [] | ELH_0002 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass boiler - boiler - wood chips - large | energy/technical data | forced outage [] | ELH_0002 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass boiler - boiler - wood chips - large | energy/technical data | forced outage [] | ELH_0002 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass boiler - boiler - wood chips - large | energy/technical data | forced outage [] | ELH_0002 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass boiler - boiler - wood chips - large | energy/technical data | forced outage [] | ELH_0002 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass boiler - boiler - wood chips - large | energy/technical data | forced outage [] | ELH_0002 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass boiler - boiler - wood chips - large | energy/technical data | forced outage [] | ELH_0002 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass boiler - boiler - wood chips - large | energy/technical data | forced outage [] | ELH_0002 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 103.43 | biomass boiler - boiler - wood chips - large | energy/technical data | generating capacity for one unit [mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 103.43 | biomass boiler - boiler - wood chips - large | energy/technical data | generating capacity for one unit [mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 103.43 | biomass boiler - boiler - wood chips - large | energy/technical data | generating capacity for one unit [mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 103.42 | biomass boiler - boiler - wood chips - large | energy/technical data | generating capacity for one unit [mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 80.92 | biomass boiler - boiler - wood chips - large | energy/technical data | generating capacity for one unit [mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 79.47 | biomass boiler - boiler - wood chips - large | energy/technical data | generating capacity for one unit [mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 103.78 | biomass boiler - boiler - wood chips - large | energy/technical data | generating capacity for one unit [mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 103.87 | biomass boiler - boiler - wood chips - large | energy/technical data | generating capacity for one unit [mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0072
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1492 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, annual average) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1492 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, annual average) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1492 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, annual average) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1492 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, annual average) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, annual average) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, annual average) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.16 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, annual average) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.16 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, annual average) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0076
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1492 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, name plate) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1492 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, name plate) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1492 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, name plate) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1492 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, name plate) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, name plate) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, name plate) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.16 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, name plate) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.16 | biomass boiler - boiler - wood chips - large | energy/technical data | heat efficiency (net, name plate) [] | ELH_0002 | tk_etd | manual_category_map | PAR_0077
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0002 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 2 | biomass boiler - boiler - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0002 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 2 | biomass boiler - boiler - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0002 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 2 | biomass boiler - boiler - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0002 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 1.7 | biomass boiler - boiler - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0002 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 1.5 | biomass boiler - boiler - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0002 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 2.3 | biomass boiler - boiler - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0002 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 2.5 | biomass boiler - boiler - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0002 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.05 | biomass boiler - boiler - wood chips - large | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.05 | biomass boiler - boiler - wood chips - large | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0.05 | biomass boiler - boiler - wood chips - large | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0.05 | biomass boiler - boiler - wood chips - large | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0.04 | biomass boiler - boiler - wood chips - large | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0.04 | biomass boiler - boiler - wood chips - large | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.06 | biomass boiler - boiler - wood chips - large | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.06 | biomass boiler - boiler - wood chips - large | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0002 | tk_etd | manual_category_map | PAR_0189
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass boiler - boiler - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass boiler - boiler - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass boiler - boiler - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass boiler - boiler - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass boiler - boiler - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass boiler - boiler - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass boiler - boiler - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass boiler - boiler - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0002 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2015 | 3 | biomass boiler - boiler - wood chips - large | environment | ch4 [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 2 | biomass boiler - boiler - wood chips - large | environment | ch4 [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 2 | biomass boiler - boiler - wood chips - large | environment | ch4 [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - large | environment | ch4 [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2020 | 1 | biomass boiler - boiler - wood chips - large | environment | ch4 [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 0 | biomass boiler - boiler - wood chips - large | environment | ch4 [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2020 | 3 | biomass boiler - boiler - wood chips - large | environment | ch4 [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 3 | biomass boiler - boiler - wood chips - large | environment | ch4 [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - large | environment | n2o [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - large | environment | n2o [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - large | environment | n2o [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 0 | biomass boiler - boiler - wood chips - large | environment | n2o [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2020 | 0 | biomass boiler - boiler - wood chips - large | environment | n2o [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 0 | biomass boiler - boiler - wood chips - large | environment | n2o [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2020 | 1 | biomass boiler - boiler - wood chips - large | environment | n2o [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 1 | biomass boiler - boiler - wood chips - large | environment | n2o [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | ctrl | 2015 | 90 | biomass boiler - boiler - wood chips - large | environment | nox [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | ctrl | 2020 | 60 | biomass boiler - boiler - wood chips - large | environment | nox [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | ctrl | 2030 | 40 | biomass boiler - boiler - wood chips - large | environment | nox [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | ctrl | 2050 | 20 | biomass boiler - boiler - wood chips - large | environment | nox [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | lower | 2020 | 40 | biomass boiler - boiler - wood chips - large | environment | nox [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | lower | 2050 | 20 | biomass boiler - boiler - wood chips - large | environment | nox [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | upper | 2020 | 60 | biomass boiler - boiler - wood chips - large | environment | nox [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | upper | 2050 | 40 | biomass boiler - boiler - wood chips - large | environment | nox [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - large | environment | particles [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 0.3 | biomass boiler - boiler - wood chips - large | environment | particles [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 0.3 | biomass boiler - boiler - wood chips - large | environment | particles [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 0.3 | biomass boiler - boiler - wood chips - large | environment | particles [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2020 | 0.1 | biomass boiler - boiler - wood chips - large | environment | particles [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 0.1 | biomass boiler - boiler - wood chips - large | environment | particles [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2020 | 2 | biomass boiler - boiler - wood chips - large | environment | particles [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 1 | biomass boiler - boiler - wood chips - large | environment | particles [g/gj_i] | ELH_0002 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9797 | biomass boiler - boiler - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0002 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9797 | biomass boiler - boiler - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0002 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9797 | biomass boiler - boiler - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0002 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.9797 | biomass boiler - boiler - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0002 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.94925 | biomass boiler - boiler - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0002 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9797 | biomass boiler - boiler - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0002 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.98985 | biomass boiler - boiler - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0002 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.98985 | biomass boiler - boiler - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0002 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2015 | 37430.7197 | biomass boiler - boiler - wood chips - large | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0002 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2020 | 36792.696 | biomass boiler - boiler - wood chips - large | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0002 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2030 | 35410.3115 | biomass boiler - boiler - wood chips - large | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0002 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2050 | 33389.9033 | biomass boiler - boiler - wood chips - large | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0002 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2020 | 31369.4952 | biomass boiler - boiler - wood chips - large | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0002 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2050 | 25095.5961 | biomass boiler - boiler - wood chips - large | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0002 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2020 | 42428.5714 | biomass boiler - boiler - wood chips - large | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0002 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2050 | 42428.5714 | biomass boiler - boiler - wood chips - large | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0002 | tk_fin | manual_category_map | PAR_0043
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.47852 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (*total) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.46788 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (*total) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.44662 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (*total) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.42535 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (*total) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.40408 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (*total) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.32965 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (*total) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.55295 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (*total) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.58485 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (*total) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0094
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.36155 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.35091 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.32965 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.32965 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.30838 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.25521 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.41472 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.44662 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0105
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.11697 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (installation) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.11697 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (installation) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.10634 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (installation) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.095704 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (installation) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.095704 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (installation) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.08507 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (installation) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.13824 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (installation) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.13824 | biomass boiler - boiler - wood chips - large | financial data | nominal investment (installation) [meur/mw_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0116
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 2.7329 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 2.8711 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 3.6261 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 3.9983 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 2.467 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 3.4772 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 3.9026 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 5.5933 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0202
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.4781 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.6163 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 2.3607 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 2.7329 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 1.5951 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 2.7116 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 2.1055 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 3.6261 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0206
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.2548 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.2548 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 1.2548 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 1.2548 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 0.87197 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0.76563 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 1.8077 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 1.9779 | biomass boiler - boiler - wood chips - large | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0002 | tk_fin | manual_category_map | PAR_0208
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8 | biomass boiler - boiler - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8 | biomass boiler - boiler - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8 | biomass boiler - boiler - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8 | biomass boiler - boiler - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8 | biomass boiler - boiler - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8 | biomass boiler - boiler - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8 | biomass boiler - boiler - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8 | biomass boiler - boiler - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.4 | biomass boiler - boiler - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.4 | biomass boiler - boiler - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.4 | biomass boiler - boiler - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.4 | biomass boiler - boiler - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.4 | biomass boiler - boiler - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.4 | biomass boiler - boiler - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.4 | biomass boiler - boiler - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.4 | biomass boiler - boiler - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1 | biomass boiler - boiler - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1 | biomass boiler - boiler - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1 | biomass boiler - boiler - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1 | biomass boiler - boiler - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1 | biomass boiler - boiler - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1 | biomass boiler - boiler - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1 | biomass boiler - boiler - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1 | biomass boiler - boiler - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0002 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 2 | biomass boiler - boiler - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 2 | biomass boiler - boiler - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 2 | biomass boiler - boiler - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 2 | biomass boiler - boiler - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 2 | biomass boiler - boiler - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 2 | biomass boiler - boiler - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 2 | biomass boiler - boiler - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 2 | biomass boiler - boiler - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0002 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.019432 | biomass boiler - boiler - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0002 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.019432 | biomass boiler - boiler - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0002 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.019432 | biomass boiler - boiler - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0002 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.019442 | biomass boiler - boiler - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0002 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01 | biomass boiler - boiler - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0002 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01 | biomass boiler - boiler - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0002 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.26 | biomass boiler - boiler - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0002 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.28 | biomass boiler - boiler - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0002 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | combustion air humidification | ELH_0002 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | combustion air humidification | ELH_0002 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | combustion air humidification | ELH_0002 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | combustion air humidification | ELH_0002 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - large | technology-specific data | combustion air humidification | ELH_0002 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - large | technology-specific data | combustion air humidification | ELH_0002 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2020 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | combustion air humidification | ELH_0002 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2050 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | combustion air humidification | ELH_0002 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 43066.5951 | biomass boiler - boiler - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0002 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 42215.8969 | biomass boiler - boiler - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0002 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 40620.8378 | biomass boiler - boiler - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0002 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 38387.7551 | biomass boiler - boiler - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0002 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 36048.3351 | biomass boiler - boiler - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0002 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 28923.7379 | biomass boiler - boiler - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0002 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 48808.8077 | biomass boiler - boiler - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0002 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 48702.4705 | biomass boiler - boiler - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0002 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2015 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | flue gas condensation | ELH_0002 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2020 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | flue gas condensation | ELH_0002 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2030 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | flue gas condensation | ELH_0002 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2050 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | flue gas condensation | ELH_0002 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - large | technology-specific data | flue gas condensation | ELH_0002 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - large | technology-specific data | flue gas condensation | ELH_0002 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2020 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | flue gas condensation | ELH_0002 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2050 | 1 | biomass boiler - boiler - wood chips - large | technology-specific data | flue gas condensation | ELH_0002 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2015 | 0.010634 | biomass boiler - boiler - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0002 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2020 | 0.010634 | biomass boiler - boiler - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0002 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2030 | 0.010634 | biomass boiler - boiler - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0002 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2050 | 0.010634 | biomass boiler - boiler - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0002 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2020 | 0.010634 | biomass boiler - boiler - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0002 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2050 | 0.010634 | biomass boiler - boiler - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0002 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2020 | 0.021267 | biomass boiler - boiler - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0002 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2050 | 0.021267 | biomass boiler - boiler - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0002 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2015 | 0.55295 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2020 | 0.53169 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2030 | 0.51042 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2050 | 0.48915 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | lower | 2020 | 0.46788 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | lower | 2050 | 0.38281 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | upper | 2020 | 0.63802 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | upper | 2050 | 0.66992 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.41472 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.40408 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.38281 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.38281 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.35091 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.28711 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.47852 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.51042 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.13824 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.1276 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.1276 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.11697 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.11697 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.095704 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.15951 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.15951 | biomass boiler - boiler - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2015 | 0.25 | biomass boiler - boiler - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2020 | 0.25 | biomass boiler - boiler - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2030 | 0.25 | biomass boiler - boiler - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2050 | 0.25 | biomass boiler - boiler - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2020 | 0 | biomass boiler - boiler - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2050 | 0 | biomass boiler - boiler - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2020 | 0.25 | biomass boiler - boiler - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2050 | 0.25 | biomass boiler - boiler - wood chips - large | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0160
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2015 | 3.1369 | biomass boiler - boiler - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2020 | 3.2965 | biomass boiler - boiler - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2030 | 4.1578 | biomass boiler - boiler - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2050 | 4.5938 | biomass boiler - boiler - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2020 | 2.8498 | biomass boiler - boiler - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2050 | 4.0089 | biomass boiler - boiler - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2020 | 3.5091 | biomass boiler - boiler - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2050 | 4.9447 | biomass boiler - boiler - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0002 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2015 | 0.020554 | biomass boiler - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2020 | 0.020554 | biomass boiler - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2030 | 0.020554 | biomass boiler - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2050 | 0.020554 | biomass boiler - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2020 | 0.017045 | biomass boiler - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2050 | 0.013836 | biomass boiler - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2020 | 0.022952 | biomass boiler - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2050 | 0.022915 | biomass boiler - boiler - wood pellets - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0005
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1 | biomass boiler - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1 | biomass boiler - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1 | biomass boiler - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1 | biomass boiler - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5 | biomass boiler - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5 | biomass boiler - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5 | biomass boiler - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5 | biomass boiler - boiler - wood pellets - small | energy/technical data | construction time [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass boiler - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0005 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass boiler - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0005 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass boiler - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0005 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass boiler - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0005 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass boiler - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0005 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass boiler - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0005 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass boiler - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0005 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass boiler - boiler - wood pellets - small | energy/technical data | forced outage [] | ELH_0005 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 6.07 | biomass boiler - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0072
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 6.07 | biomass boiler - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0072
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 6.07 | biomass boiler - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0072
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 6.07 | biomass boiler - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0072
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 5.45 | biomass boiler - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0072
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 5.37 | biomass boiler - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0072
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 6.09 | biomass boiler - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0072
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 6.1 | biomass boiler - boiler - wood pellets - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0072
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.0117 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.0117 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.0117 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.0117 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.9 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.89 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.02 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.02 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0076
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.0117 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.0117 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.0117 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.0117 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.9 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.89 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.02 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.02 | biomass boiler - boiler - wood pellets - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0005 | tk_etd | manual_category_map | PAR_0077
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass boiler - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0005 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass boiler - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0005 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass boiler - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0005 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass boiler - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0005 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55 | biomass boiler - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0005 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25 | biomass boiler - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0005 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45 | biomass boiler - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0005 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75 | biomass boiler - boiler - wood pellets - small | energy/technical data | planned outage [weeks per year] | ELH_0005 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.16 | biomass boiler - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0189
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.16 | biomass boiler - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0189
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0.16 | biomass boiler - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0189
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0.16 | biomass boiler - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0189
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0.14 | biomass boiler - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0189
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0.12 | biomass boiler - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0189
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.19 | biomass boiler - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0189
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.21 | biomass boiler - boiler - wood pellets - small | energy/technical data | space requirement [1000 m2/mw_h] | ELH_0005 | tk_etd | manual_category_map | PAR_0189
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass boiler - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass boiler - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass boiler - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass boiler - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass boiler - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass boiler - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass boiler - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass boiler - boiler - wood pellets - small | energy/technical data | technical lifetime [years] | ELH_0005 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 0 | biomass boiler - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 0 | biomass boiler - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 0 | biomass boiler - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 0 | biomass boiler - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 0 | biomass boiler - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 0 | biomass boiler - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 0 | biomass boiler - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 0 | biomass boiler - boiler - wood pellets - small | environment | ch4 [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 1.2 | biomass boiler - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 1 | biomass boiler - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 1 | biomass boiler - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 1 | biomass boiler - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 1 | biomass boiler - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 0 | biomass boiler - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 3 | biomass boiler - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 1 | biomass boiler - boiler - wood pellets - small | environment | n2o [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 90 | biomass boiler - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 50 | biomass boiler - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 40 | biomass boiler - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 40 | biomass boiler - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 40 | biomass boiler - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 20 | biomass boiler - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 70 | biomass boiler - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 40 | biomass boiler - boiler - wood pellets - small | environment | nox [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 2 | biomass boiler - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 0.3 | biomass boiler - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 0.3 | biomass boiler - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 0.3 | biomass boiler - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 0.1 | biomass boiler - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 0.1 | biomass boiler - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 2 | biomass boiler - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 1 | biomass boiler - boiler - wood pellets - small | environment | particles [g/gj_i] | ELH_0005 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9825 | biomass boiler - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0005 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9825 | biomass boiler - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0005 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9825 | biomass boiler - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0005 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.9825 | biomass boiler - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0005 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.9125 | biomass boiler - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0005 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9825 | biomass boiler - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0005 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.99125 | biomass boiler - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0005 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.99125 | biomass boiler - boiler - wood pellets - small | environment | so2 (degree of desulphuring) [] | ELH_0005 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2015 | 35729.3233 | biomass boiler - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0005 | tk_fin | manual_category_map | PAR_0043
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2020 | 34772.2879 | biomass boiler - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0005 | tk_fin | manual_category_map | PAR_0043
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2030 | 32964.5543 | biomass boiler - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0005 | tk_fin | manual_category_map | PAR_0043
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2050 | 29668.0988 | biomass boiler - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0005 | tk_fin | manual_category_map | PAR_0043
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2020 | 29774.4361 | biomass boiler - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0005 | tk_fin | manual_category_map | PAR_0043
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2050 | 23075.188 | biomass boiler - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0005 | tk_fin | manual_category_map | PAR_0043
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2020 | 40301.826 | biomass boiler - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0005 | tk_fin | manual_category_map | PAR_0043
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2050 | 39451.1278 | biomass boiler - boiler - wood pellets - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0005 | tk_fin | manual_category_map | PAR_0043
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.77626 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0094
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.75499 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0094
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.72309 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0094
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.64866 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0094
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.65929 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0094
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.54232 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0094
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.89323 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0094
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.95704 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0094
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.46788 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0105
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.45725 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0105
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.43598 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0105
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.39345 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0105
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.40408 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0105
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.32965 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0105
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.54232 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0105
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.60612 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0105
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.30838 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0116
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.29774 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0116
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.28711 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0116
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.25521 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0116
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.25521 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0116
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.21267 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0116
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.35091 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0116
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.35091 | biomass boiler - boiler - wood pellets - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0116
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2015 | 1.9566 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0202
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2020 | 2.0842 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0202
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2030 | 2.786 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0202
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2050 | 3.1369 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0202
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2020 | 1.9247 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0202
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2050 | 2.9136 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0202
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2020 | 2.4458 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0202
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2050 | 3.7431 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0202
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2015 | 1.3718 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0206
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2020 | 1.51 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0206
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2030 | 2.2118 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0206
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2050 | 2.5521 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0206
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2020 | 1.4887 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0206
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2050 | 2.5202 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0206
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2020 | 1.712 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0206
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2050 | 2.9455 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0206
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2015 | 0.57422 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0208
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2020 | 0.57422 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0208
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2030 | 0.57422 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0208
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2050 | 0.57422 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0208
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2020 | 0.43598 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0208
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2050 | 0.38281 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0208
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2020 | 0.73373 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0208
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2050 | 0.79753 | biomass boiler - boiler - wood pellets - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0005 | tk_fin | manual_category_map | PAR_0208
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5 | biomass boiler - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5 | biomass boiler - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5 | biomass boiler - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5 | biomass boiler - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5 | biomass boiler - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5 | biomass boiler - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5 | biomass boiler - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5 | biomass boiler - boiler - wood pellets - small | regulation ability | cold start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2015 | 0.4 | biomass boiler - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2020 | 0.4 | biomass boiler - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2030 | 0.4 | biomass boiler - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2050 | 0.4 | biomass boiler - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2020 | 0.4 | biomass boiler - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2050 | 0.4 | biomass boiler - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2020 | 0.4 | biomass boiler - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2050 | 0.4 | biomass boiler - boiler - wood pellets - small | regulation ability | minimum load (of full load) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1 | biomass boiler - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1 | biomass boiler - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1 | biomass boiler - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1 | biomass boiler - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1 | biomass boiler - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1 | biomass boiler - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1 | biomass boiler - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1 | biomass boiler - boiler - wood pellets - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0005 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 0.25 | biomass boiler - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 0.25 | biomass boiler - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 0.25 | biomass boiler - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 0.25 | biomass boiler - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 0.25 | biomass boiler - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 0.25 | biomass boiler - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 0.25 | biomass boiler - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 0.25 | biomass boiler - boiler - wood pellets - small | regulation ability | warm start-up time [hours] | ELH_0005 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.01729 | biomass boiler - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0005 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.01729 | biomass boiler - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0005 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.01729 | biomass boiler - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0005 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.01729 | biomass boiler - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0005 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01 | biomass boiler - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0005 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01 | biomass boiler - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0005 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.11 | biomass boiler - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0005 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.13 | biomass boiler - boiler - wood pellets - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0005 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2015 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0005 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2020 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0005 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2030 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0005 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2050 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0005 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2020 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0005 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2050 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0005 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2020 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0005 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2050 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | combustion air humidification | ELH_0005 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 36154.6724 | biomass boiler - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0005 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 35197.6369 | biomass boiler - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0005 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 33283.5661 | biomass boiler - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0005 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 30093.4479 | biomass boiler - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0005 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 30093.4479 | biomass boiler - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0005 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 23287.8625 | biomass boiler - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0005 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 40727.1751 | biomass boiler - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0005 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 39876.4769 | biomass boiler - boiler - wood pellets - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0005 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2015 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0005 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2020 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0005 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2030 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0005 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2050 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0005 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2020 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0005 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2050 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0005 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2020 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0005 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2050 | 1 | biomass boiler - boiler - wood pellets - small | technology-specific data | flue gas condensation | ELH_0005 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2015 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0005 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2020 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0005 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2030 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0005 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2050 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0005 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2020 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0005 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2050 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0005 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2020 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0005 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2050 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0005 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2015 | 0.7869 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2020 | 0.76563 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2030 | 0.73373 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2050 | 0.65929 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | lower | 2020 | 0.66992 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | lower | 2050 | 0.55295 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | upper | 2020 | 0.90387 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | upper | 2050 | 0.96767 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.47852 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.46788 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.44662 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.40408 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.40408 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.32965 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.55295 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.60612 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.30838 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.29774 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.28711 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.25521 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.26584 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.21267 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.36155 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.36155 | biomass boiler - boiler - wood pellets - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2015 | 0.06 | biomass boiler - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2020 | 0.06 | biomass boiler - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2030 | 0.06 | biomass boiler - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2050 | 0.06 | biomass boiler - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2020 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2050 | 0 | biomass boiler - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2020 | 0.06 | biomass boiler - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2050 | 0.06 | biomass boiler - boiler - wood pellets - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0160
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2015 | 1.9779 | biomass boiler - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2020 | 2.1055 | biomass boiler - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2030 | 2.8179 | biomass boiler - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2050 | 3.1689 | biomass boiler - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2020 | 1.9566 | biomass boiler - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2050 | 2.9562 | biomass boiler - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2020 | 2.2224 | biomass boiler - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2050 | 3.3496 | biomass boiler - boiler - wood pellets - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0005 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | ctrl | 2015 | 0.020956 | biomass boiler - boiler - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | ctrl | 2020 | 0.020956 | biomass boiler - boiler - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | ctrl | 2030 | 0.020956 | biomass boiler - boiler - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | ctrl | 2050 | 0.020956 | biomass boiler - boiler - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | lower | 2020 | 0.018096 | biomass boiler - boiler - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | lower | 2050 | 0.014478 | biomass boiler - boiler - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | upper | 2020 | 0.02338 | biomass boiler - boiler - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | upper | 2050 | 0.023357 | biomass boiler - boiler - straw - small | energy/technical data | auxiliary electricity consumption (share of heat gen.) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0005
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1 | biomass boiler - boiler - straw - small | energy/technical data | construction time [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1 | biomass boiler - boiler - straw - small | energy/technical data | construction time [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1 | biomass boiler - boiler - straw - small | energy/technical data | construction time [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1 | biomass boiler - boiler - straw - small | energy/technical data | construction time [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5 | biomass boiler - boiler - straw - small | energy/technical data | construction time [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5 | biomass boiler - boiler - straw - small | energy/technical data | construction time [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5 | biomass boiler - boiler - straw - small | energy/technical data | construction time [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5 | biomass boiler - boiler - straw - small | energy/technical data | construction time [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0026
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.04 | biomass boiler - boiler - straw - small | energy/technical data | forced outage [] | ELH_0001 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.04 | biomass boiler - boiler - straw - small | energy/technical data | forced outage [] | ELH_0001 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.04 | biomass boiler - boiler - straw - small | energy/technical data | forced outage [] | ELH_0001 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.04 | biomass boiler - boiler - straw - small | energy/technical data | forced outage [] | ELH_0001 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.04 | biomass boiler - boiler - straw - small | energy/technical data | forced outage [] | ELH_0001 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.04 | biomass boiler - boiler - straw - small | energy/technical data | forced outage [] | ELH_0001 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.04 | biomass boiler - boiler - straw - small | energy/technical data | forced outage [] | ELH_0001 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.04 | biomass boiler - boiler - straw - small | energy/technical data | forced outage [] | ELH_0001 | tk_etd | manual_category_map | PAR_0065
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 6.19 | biomass boiler - boiler - straw - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0001 | tk_etd | manual_category_map | PAR_0072
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 6.19 | biomass boiler - boiler - straw - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0001 | tk_etd | manual_category_map | PAR_0072
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 6.19 | biomass boiler - boiler - straw - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0001 | tk_etd | manual_category_map | PAR_0072
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 6.19 | biomass boiler - boiler - straw - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0001 | tk_etd | manual_category_map | PAR_0072
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 5.34 | biomass boiler - boiler - straw - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0001 | tk_etd | manual_category_map | PAR_0072
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 5.34 | biomass boiler - boiler - straw - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0001 | tk_etd | manual_category_map | PAR_0072
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 6.22 | biomass boiler - boiler - straw - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0001 | tk_etd | manual_category_map | PAR_0072
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 6.22 | biomass boiler - boiler - straw - small | energy/technical data | generating capacity for one unit [mw_h] | ELH_0001 | tk_etd | manual_category_map | PAR_0072
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.0323 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0076
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.0323 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0076
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.0323 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0076
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.0323 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0076
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.88 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0076
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0076
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.04 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0076
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.04 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, annual average) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0076
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.0323 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0077
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.0323 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0077
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.0323 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0077
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.0323 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0077
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.88 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0077
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0077
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.04 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0077
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.04 | biomass boiler - boiler - straw - small | energy/technical data | heat efficiency (net, name plate) [] | ELH_0001 | tk_etd | manual_category_map | PAR_0077
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 4 | biomass boiler - boiler - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0001 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 4 | biomass boiler - boiler - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0001 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 4 | biomass boiler - boiler - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0001 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 4 | biomass boiler - boiler - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0001 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 3.4 | biomass boiler - boiler - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0001 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 3 | biomass boiler - boiler - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0001 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 4.6 | biomass boiler - boiler - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0001 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 5 | biomass boiler - boiler - straw - small | energy/technical data | planned outage [weeks per year] | ELH_0001 | tk_etd | manual_category_map | PAR_0168
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.24 | biomass boiler - boiler - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0001 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.24 | biomass boiler - boiler - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0001 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.24 | biomass boiler - boiler - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0001 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.24 | biomass boiler - boiler - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0001 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.21 | biomass boiler - boiler - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0001 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.18 | biomass boiler - boiler - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0001 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.28 | biomass boiler - boiler - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0001 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.3 | biomass boiler - boiler - straw - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0001 | tk_etd | manual_category_map | PAR_0188
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass boiler - boiler - straw - small | energy/technical data | technical lifetime [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass boiler - boiler - straw - small | energy/technical data | technical lifetime [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass boiler - boiler - straw - small | energy/technical data | technical lifetime [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass boiler - boiler - straw - small | energy/technical data | technical lifetime [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20 | biomass boiler - boiler - straw - small | energy/technical data | technical lifetime [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20 | biomass boiler - boiler - straw - small | energy/technical data | technical lifetime [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35 | biomass boiler - boiler - straw - small | energy/technical data | technical lifetime [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35 | biomass boiler - boiler - straw - small | energy/technical data | technical lifetime [years] | ELH_0001 | tk_etd | manual_category_map | PAR_0198
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 16 | biomass boiler - boiler - straw - small | environment | ch4 [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 11 | biomass boiler - boiler - straw - small | environment | ch4 [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 8 | biomass boiler - boiler - straw - small | environment | ch4 [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 4 | biomass boiler - boiler - straw - small | environment | ch4 [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 4 | biomass boiler - boiler - straw - small | environment | ch4 [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 2 | biomass boiler - boiler - straw - small | environment | ch4 [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 16 | biomass boiler - boiler - straw - small | environment | ch4 [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 16 | biomass boiler - boiler - straw - small | environment | ch4 [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0018
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 4 | biomass boiler - boiler - straw - small | environment | n2o [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 3 | biomass boiler - boiler - straw - small | environment | n2o [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 2 | biomass boiler - boiler - straw - small | environment | n2o [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 1 | biomass boiler - boiler - straw - small | environment | n2o [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 1 | biomass boiler - boiler - straw - small | environment | n2o [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 1 | biomass boiler - boiler - straw - small | environment | n2o [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 4 | biomass boiler - boiler - straw - small | environment | n2o [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 4 | biomass boiler - boiler - straw - small | environment | n2o [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0089
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 90 | biomass boiler - boiler - straw - small | environment | nox [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 70 | biomass boiler - boiler - straw - small | environment | nox [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 70 | biomass boiler - boiler - straw - small | environment | nox [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 70 | biomass boiler - boiler - straw - small | environment | nox [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 40 | biomass boiler - boiler - straw - small | environment | nox [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 20 | biomass boiler - boiler - straw - small | environment | nox [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 90 | biomass boiler - boiler - straw - small | environment | nox [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 70 | biomass boiler - boiler - straw - small | environment | nox [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0152
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 2 | biomass boiler - boiler - straw - small | environment | particles [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 0.3 | biomass boiler - boiler - straw - small | environment | particles [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 0.3 | biomass boiler - boiler - straw - small | environment | particles [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 0.3 | biomass boiler - boiler - straw - small | environment | particles [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 0.1 | biomass boiler - boiler - straw - small | environment | particles [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 0.1 | biomass boiler - boiler - straw - small | environment | particles [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 2 | biomass boiler - boiler - straw - small | environment | particles [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 1 | biomass boiler - boiler - straw - small | environment | particles [g/gj_i] | ELH_0001 | tk_env | manual_category_map | PAR_0163
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9545 | biomass boiler - boiler - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0001 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9636 | biomass boiler - boiler - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0001 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9909 | biomass boiler - boiler - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0001 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.99818 | biomass boiler - boiler - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0001 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.909 | biomass boiler - boiler - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0001 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9545 | biomass boiler - boiler - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0001 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.99818 | biomass boiler - boiler - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0001 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.99909 | biomass boiler - boiler - straw - small | environment | so2 (degree of desulphuring) [] | ELH_0001 | tk_env | manual_category_map | PAR_0181
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2015 | 55614.3932 | biomass boiler - boiler - straw - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0001 | tk_fin | manual_category_map | PAR_0043
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2020 | 54019.3341 | biomass boiler - boiler - straw - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0001 | tk_fin | manual_category_map | PAR_0043
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2030 | 50935.5532 | biomass boiler - boiler - straw - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0001 | tk_fin | manual_category_map | PAR_0043
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2050 | 45618.6896 | biomass boiler - boiler - straw - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0001 | tk_fin | manual_category_map | PAR_0043
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2020 | 46150.376 | biomass boiler - boiler - straw - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0001 | tk_fin | manual_category_map | PAR_0043
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2050 | 34878.6252 | biomass boiler - boiler - straw - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0001 | tk_fin | manual_category_map | PAR_0043
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2020 | 63377.014 | biomass boiler - boiler - straw - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0001 | tk_fin | manual_category_map | PAR_0043
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2050 | 59229.8604 | biomass boiler - boiler - straw - small | financial data | fixed o&m (*total) [eur/mw_h/y] | ELH_0001 | tk_fin | manual_category_map | PAR_0043
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2015 | 0.95704 | biomass boiler - boiler - straw - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0094
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2020 | 0.93577 | biomass boiler - boiler - straw - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0094
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2030 | 0.8826 | biomass boiler - boiler - straw - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0094
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2050 | 0.79753 | biomass boiler - boiler - straw - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0094
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2020 | 0.80816 | biomass boiler - boiler - straw - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0094
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2050 | 0.65929 | biomass boiler - boiler - straw - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0094
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2020 | 1.1484 | biomass boiler - boiler - straw - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0094
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2050 | 1.1591 | biomass boiler - boiler - straw - small | financial data | nominal investment (*total) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0094
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2015 | 0.46788 | biomass boiler - boiler - straw - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0105
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2020 | 0.45725 | biomass boiler - boiler - straw - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0105
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2030 | 0.42535 | biomass boiler - boiler - straw - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0105
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2050 | 0.39345 | biomass boiler - boiler - straw - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0105
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2020 | 0.39345 | biomass boiler - boiler - straw - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0105
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2050 | 0.31901 | biomass boiler - boiler - straw - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0105
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2020 | 0.58485 | biomass boiler - boiler - straw - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0105
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2050 | 0.58485 | biomass boiler - boiler - straw - small | financial data | nominal investment (equipment) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0105
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2015 | 0.48915 | biomass boiler - boiler - straw - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0116
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2020 | 0.47852 | biomass boiler - boiler - straw - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0116
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2030 | 0.45725 | biomass boiler - boiler - straw - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0116
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2050 | 0.41472 | biomass boiler - boiler - straw - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0116
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2020 | 0.41472 | biomass boiler - boiler - straw - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0116
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2050 | 0.34028 | biomass boiler - boiler - straw - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0116
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2020 | 0.56359 | biomass boiler - boiler - straw - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0116
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2050 | 0.57422 | biomass boiler - boiler - straw - small | financial data | nominal investment (installation) [meur/mw_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0116
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2015 | 2.1161 | biomass boiler - boiler - straw - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0202
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2020 | 2.2437 | biomass boiler - boiler - straw - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0202
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2030 | 2.9562 | biomass boiler - boiler - straw - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0202
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2050 | 3.3177 | biomass boiler - boiler - straw - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0202
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2020 | 2.0417 | biomass boiler - boiler - straw - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0202
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2050 | 3.0412 | biomass boiler - boiler - straw - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0202
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2020 | 2.7541 | biomass boiler - boiler - straw - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0202
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2050 | 4.0834 | biomass boiler - boiler - straw - small | financial data | variable o&m (*total) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0202
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2015 | 1.4037 | biomass boiler - boiler - straw - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0206
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2020 | 1.5419 | biomass boiler - boiler - straw - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0206
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2030 | 2.2544 | biomass boiler - boiler - straw - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0206
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2050 | 2.6053 | biomass boiler - boiler - straw - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0206
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2020 | 1.5206 | biomass boiler - boiler - straw - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0206
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2050 | 2.5734 | biomass boiler - boiler - straw - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0206
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2020 | 1.8184 | biomass boiler - boiler - straw - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0206
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2050 | 3.0838 | biomass boiler - boiler - straw - small | financial data | variable o&m (electricity cost) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0206
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2015 | 0.71246 | biomass boiler - boiler - straw - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0208
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2020 | 0.71246 | biomass boiler - boiler - straw - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0208
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2030 | 0.71246 | biomass boiler - boiler - straw - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0208
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2050 | 0.71246 | biomass boiler - boiler - straw - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0208
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2020 | 0.52105 | biomass boiler - boiler - straw - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0208
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2050 | 0.45725 | biomass boiler - boiler - straw - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0208
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2020 | 0.93577 | biomass boiler - boiler - straw - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0208
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2050 | 0.99957 | biomass boiler - boiler - straw - small | financial data | variable o&m (other o&m) [eur/mwh_h] | ELH_0001 | tk_fin | manual_category_map | PAR_0208
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | cold start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | cold start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | cold start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | cold start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | cold start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | cold start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | cold start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | cold start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0022
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2015 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | minimum load (of full load) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2020 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | minimum load (of full load) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2030 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | minimum load (of full load) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2050 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | minimum load (of full load) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2020 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | minimum load (of full load) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2050 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | minimum load (of full load) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2020 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | minimum load (of full load) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2050 | 0.5 | biomass boiler - boiler - straw - small | regulation ability | minimum load (of full load) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0085
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1 | biomass boiler - boiler - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1 | biomass boiler - boiler - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1 | biomass boiler - boiler - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1 | biomass boiler - boiler - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1 | biomass boiler - boiler - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1 | biomass boiler - boiler - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1 | biomass boiler - boiler - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1 | biomass boiler - boiler - straw - small | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0001 | tk_reg | manual_category_map | PAR_0179
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 0.25 | biomass boiler - boiler - straw - small | regulation ability | warm start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 0.25 | biomass boiler - boiler - straw - small | regulation ability | warm start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 0.25 | biomass boiler - boiler - straw - small | regulation ability | warm start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 0.25 | biomass boiler - boiler - straw - small | regulation ability | warm start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 0.25 | biomass boiler - boiler - straw - small | regulation ability | warm start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 0.25 | biomass boiler - boiler - straw - small | regulation ability | warm start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 0.25 | biomass boiler - boiler - straw - small | regulation ability | warm start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 0.25 | biomass boiler - boiler - straw - small | regulation ability | warm start-up time [hours] | ELH_0001 | tk_reg | manual_category_map | PAR_0211
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.017669 | biomass boiler - boiler - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0001 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.017669 | biomass boiler - boiler - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0001 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.017669 | biomass boiler - boiler - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0001 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.017669 | biomass boiler - boiler - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0001 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01 | biomass boiler - boiler - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0001 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01 | biomass boiler - boiler - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0001 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.15 | biomass boiler - boiler - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0001 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.15 | biomass boiler - boiler - straw - small | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0001 | tk_tsd | manual_category_map | PAR_0003
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | ctrl | 2015 | 1 | biomass boiler - boiler - straw - small | technology-specific data | combustion air humidification | ELH_0001 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | ctrl | 2020 | 1 | biomass boiler - boiler - straw - small | technology-specific data | combustion air humidification | ELH_0001 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | ctrl | 2030 | 1 | biomass boiler - boiler - straw - small | technology-specific data | combustion air humidification | ELH_0001 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | ctrl | 2050 | 1 | biomass boiler - boiler - straw - small | technology-specific data | combustion air humidification | ELH_0001 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | lower | 2020 | 0 | biomass boiler - boiler - straw - small | technology-specific data | combustion air humidification | ELH_0001 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | lower | 2050 | 0 | biomass boiler - boiler - straw - small | technology-specific data | combustion air humidification | ELH_0001 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | upper | 2020 | 1 | biomass boiler - boiler - straw - small | technology-specific data | combustion air humidification | ELH_0001 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | upper | 2050 | 1 | biomass boiler - boiler - straw - small | technology-specific data | combustion air humidification | ELH_0001 | tk_tsd | manual_category_map | PAR_0025
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 57422.1267 | biomass boiler - boiler - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0001 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 55720.7304 | biomass boiler - boiler - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0001 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 52530.6122 | biomass boiler - boiler - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0001 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 47001.0741 | biomass boiler - boiler - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0001 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 47639.0977 | biomass boiler - boiler - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0001 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 36048.3351 | biomass boiler - boiler - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0001 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 65503.7594 | biomass boiler - boiler - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0001 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 61143.9313 | biomass boiler - boiler - straw - small | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0001 | tk_tsd | manual_category_map | PAR_0044
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | ctrl | 2015 | 1 | biomass boiler - boiler - straw - small | technology-specific data | flue gas condensation | ELH_0001 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | ctrl | 2020 | 1 | biomass boiler - boiler - straw - small | technology-specific data | flue gas condensation | ELH_0001 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | ctrl | 2030 | 1 | biomass boiler - boiler - straw - small | technology-specific data | flue gas condensation | ELH_0001 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | ctrl | 2050 | 1 | biomass boiler - boiler - straw - small | technology-specific data | flue gas condensation | ELH_0001 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | lower | 2020 | 0 | biomass boiler - boiler - straw - small | technology-specific data | flue gas condensation | ELH_0001 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | lower | 2050 | 0 | biomass boiler - boiler - straw - small | technology-specific data | flue gas condensation | ELH_0001 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | upper | 2020 | 1 | biomass boiler - boiler - straw - small | technology-specific data | flue gas condensation | ELH_0001 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | upper | 2050 | 1 | biomass boiler - boiler - straw - small | technology-specific data | flue gas condensation | ELH_0001 | tk_tsd | manual_category_map | PAR_0062
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.08507 | biomass boiler - boiler - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0001 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.08507 | biomass boiler - boiler - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0001 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.074436 | biomass boiler - boiler - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0001 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.074436 | biomass boiler - boiler - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0001 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.074436 | biomass boiler - boiler - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0001 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.063802 | biomass boiler - boiler - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0001 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.095704 | biomass boiler - boiler - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0001 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.095704 | biomass boiler - boiler - straw - small | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0001 | tk_tsd | manual_category_map | PAR_0066
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | ctrl | 2015 | 0.98894 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | ctrl | 2020 | 0.95704 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | ctrl | 2030 | 0.9145 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | ctrl | 2050 | 0.82943 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | lower | 2020 | 0.84006 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | lower | 2050 | 0.68056 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | upper | 2020 | 1.191 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | upper | 2050 | 1.191 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0095
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.47852 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.46788 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.44662 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.40408 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.40408 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.32965 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.60612 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.60612 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0106
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.51042 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.48915 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.46788 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.42535 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.43598 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.35091 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.58485 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.58485 | biomass boiler - boiler - straw - small | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0117
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | ctrl | 2015 | 0.09 | biomass boiler - boiler - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | ctrl | 2020 | 0.09 | biomass boiler - boiler - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | ctrl | 2030 | 0.09 | biomass boiler - boiler - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | ctrl | 2050 | 0.09 | biomass boiler - boiler - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | lower | 2020 | 0 | biomass boiler - boiler - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | lower | 2050 | 0 | biomass boiler - boiler - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | upper | 2020 | 0.09 | biomass boiler - boiler - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | upper | 2050 | 0.09 | biomass boiler - boiler - straw - small | technology-specific data | output of recovered condensate [t/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0160
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 2.1799 | biomass boiler - boiler - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 2.3182 | biomass boiler - boiler - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 3.0519 | biomass boiler - boiler - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 3.4241 | biomass boiler - boiler - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 2.1161 | biomass boiler - boiler - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 3.1476 | biomass boiler - boiler - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 2.4458 | biomass boiler - boiler - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0203
ELH | 09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 3.6367 | biomass boiler - boiler - straw - small | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0001 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.44 | biomass chp - extraction - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.45 | biomass chp - extraction - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.42 | biomass chp - extraction - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.4 | biomass chp - extraction - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.42 | biomass chp - extraction - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.43 | biomass chp - extraction - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.41 | biomass chp - extraction - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.44 | biomass chp - extraction - wood chips - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0015
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5 | biomass chp - extraction - wood chips - large | energy/technical data | construction time [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5 | biomass chp - extraction - wood chips - large | energy/technical data | construction time [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5 | biomass chp - extraction - wood chips - large | energy/technical data | construction time [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5 | biomass chp - extraction - wood chips - large | energy/technical data | construction time [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 5 | biomass chp - extraction - wood chips - large | energy/technical data | construction time [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 5 | biomass chp - extraction - wood chips - large | energy/technical data | construction time [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5 | biomass chp - extraction - wood chips - large | energy/technical data | construction time [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5 | biomass chp - extraction - wood chips - large | energy/technical data | construction time [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0026
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.14 | biomass chp - extraction - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.14 | biomass chp - extraction - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.14 | biomass chp - extraction - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.13 | biomass chp - extraction - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.13 | biomass chp - extraction - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.13 | biomass chp - extraction - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.13 | biomass chp - extraction - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.14 | biomass chp - extraction - wood chips - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0012 | tk_etd | manual_category_map | PAR_0028
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.408 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.409 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.41 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.394 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.378 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.385 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.41 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.414 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0034
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.43 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.43 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.432 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.414 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.398 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.404 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.431 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.436 | biomass chp - extraction - wood chips - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0012 | tk_etd | manual_category_map | PAR_0036
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp - extraction - wood chips - large | energy/technical data | forced outage [] | ELH_0012 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp - extraction - wood chips - large | energy/technical data | forced outage [] | ELH_0012 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp - extraction - wood chips - large | energy/technical data | forced outage [] | ELH_0012 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp - extraction - wood chips - large | energy/technical data | forced outage [] | ELH_0012 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp - extraction - wood chips - large | energy/technical data | forced outage [] | ELH_0012 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp - extraction - wood chips - large | energy/technical data | forced outage [] | ELH_0012 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp - extraction - wood chips - large | energy/technical data | forced outage [] | ELH_0012 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp - extraction - wood chips - large | energy/technical data | forced outage [] | ELH_0012 | tk_etd | manual_category_map | PAR_0065
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 257.7 | biomass chp - extraction - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 258.2 | biomass chp - extraction - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 259.7 | biomass chp - extraction - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 248.6 | biomass chp - extraction - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 238.8 | biomass chp - extraction - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 242.6 | biomass chp - extraction - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 258.6 | biomass chp - extraction - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 261.3 | biomass chp - extraction - wood chips - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0071
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp - extraction - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0012 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp - extraction - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0012 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp - extraction - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0012 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp - extraction - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0012 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.6 | biomass chp - extraction - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0012 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.3 | biomass chp - extraction - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0012 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.5 | biomass chp - extraction - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0012 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.8 | biomass chp - extraction - wood chips - large | energy/technical data | planned outage [weeks per year] | ELH_0012 | tk_etd | manual_category_map | PAR_0168
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.06 | biomass chp - extraction - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.06 | biomass chp - extraction - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.06 | biomass chp - extraction - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.06 | biomass chp - extraction - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.06 | biomass chp - extraction - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.06 | biomass chp - extraction - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.06 | biomass chp - extraction - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.06 | biomass chp - extraction - wood chips - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0012 | tk_etd | manual_category_map | PAR_0188
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp - extraction - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp - extraction - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp - extraction - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp - extraction - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 25 | biomass chp - extraction - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 25 | biomass chp - extraction - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 25 | biomass chp - extraction - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 25 | biomass chp - extraction - wood chips - large | energy/technical data | technical lifetime [years] | ELH_0012 | tk_etd | manual_category_map | PAR_0198
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3 | biomass chp - extraction - wood chips - large | environment | ch4 [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2 | biomass chp - extraction - wood chips - large | environment | ch4 [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2 | biomass chp - extraction - wood chips - large | environment | ch4 [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1 | biomass chp - extraction - wood chips - large | environment | ch4 [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1 | biomass chp - extraction - wood chips - large | environment | ch4 [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0 | biomass chp - extraction - wood chips - large | environment | ch4 [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3 | biomass chp - extraction - wood chips - large | environment | ch4 [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3 | biomass chp - extraction - wood chips - large | environment | ch4 [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0018
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10 | biomass chp - extraction - wood chips - large | environment | n2o [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8 | biomass chp - extraction - wood chips - large | environment | n2o [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6 | biomass chp - extraction - wood chips - large | environment | n2o [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5 | biomass chp - extraction - wood chips - large | environment | n2o [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5 | biomass chp - extraction - wood chips - large | environment | n2o [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3 | biomass chp - extraction - wood chips - large | environment | n2o [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10 | biomass chp - extraction - wood chips - large | environment | n2o [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10 | biomass chp - extraction - wood chips - large | environment | n2o [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0089
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30 | biomass chp - extraction - wood chips - large | environment | nox [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20 | biomass chp - extraction - wood chips - large | environment | nox [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20 | biomass chp - extraction - wood chips - large | environment | nox [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10 | biomass chp - extraction - wood chips - large | environment | nox [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10 | biomass chp - extraction - wood chips - large | environment | nox [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10 | biomass chp - extraction - wood chips - large | environment | nox [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30 | biomass chp - extraction - wood chips - large | environment | nox [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20 | biomass chp - extraction - wood chips - large | environment | nox [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0152
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3 | biomass chp - extraction - wood chips - large | environment | particles [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3 | biomass chp - extraction - wood chips - large | environment | particles [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3 | biomass chp - extraction - wood chips - large | environment | particles [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3 | biomass chp - extraction - wood chips - large | environment | particles [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1 | biomass chp - extraction - wood chips - large | environment | particles [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1 | biomass chp - extraction - wood chips - large | environment | particles [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2 | biomass chp - extraction - wood chips - large | environment | particles [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1 | biomass chp - extraction - wood chips - large | environment | particles [g/gj_i] | ELH_0012 | tk_env | manual_category_map | PAR_0163
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2015 | 0.975 | biomass chp - extraction - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0012 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2020 | 0.975 | biomass chp - extraction - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0012 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2030 | 0.975 | biomass chp - extraction - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0012 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2050 | 0.975 | biomass chp - extraction - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0012 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2020 | 0.975 | biomass chp - extraction - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0012 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2050 | 0.975 | biomass chp - extraction - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0012 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2020 | 0.975 | biomass chp - extraction - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0012 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2050 | 0.975 | biomass chp - extraction - wood chips - large | environment | so2 (degree of desulphuring) [] | ELH_0012 | tk_env | manual_category_map | PAR_0181
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 74436.0903 | biomass chp - extraction - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0012 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 73372.7175 | biomass chp - extraction - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0012 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 68055.854 | biomass chp - extraction - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0012 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 65929.1085 | biomass chp - extraction - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0012 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 70182.5994 | biomass chp - extraction - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0012 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 60612.2449 | biomass chp - extraction - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0012 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 85069.8174 | biomass chp - extraction - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0012 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 84006.4447 | biomass chp - extraction - wood chips - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0012 | tk_fin | manual_category_map | PAR_0042
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.7648 | biomass chp - extraction - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.6584 | biomass chp - extraction - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.5521 | biomass chp - extraction - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.4458 | biomass chp - extraction - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.5521 | biomass chp - extraction - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.3394 | biomass chp - extraction - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 3.2965 | biomass chp - extraction - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 3.5091 | biomass chp - extraction - wood chips - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0093
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.7014 | biomass chp - extraction - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.7014 | biomass chp - extraction - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.5951 | biomass chp - extraction - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.4887 | biomass chp - extraction - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.5951 | biomass chp - extraction - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.4887 | biomass chp - extraction - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.0204 | biomass chp - extraction - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 2.2331 | biomass chp - extraction - wood chips - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0104
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.0634 | biomass chp - extraction - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0.95704 | biomass chp - extraction - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0.95704 | biomass chp - extraction - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.8507 | biomass chp - extraction - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0.8507 | biomass chp - extraction - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.8507 | biomass chp - extraction - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.1697 | biomass chp - extraction - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.276 | biomass chp - extraction - wood chips - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0115
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 2.7648 | biomass chp - extraction - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 2.7648 | biomass chp - extraction - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 2.7648 | biomass chp - extraction - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 2.8711 | biomass chp - extraction - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 2.9774 | biomass chp - extraction - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 2.8711 | biomass chp - extraction - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.7648 | biomass chp - extraction - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.6584 | biomass chp - extraction - wood chips - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0012 | tk_fin | manual_category_map | PAR_0201
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 12 | biomass chp - extraction - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 12 | biomass chp - extraction - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 12 | biomass chp - extraction - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 12 | biomass chp - extraction - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 12 | biomass chp - extraction - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 12 | biomass chp - extraction - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 12 | biomass chp - extraction - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 12 | biomass chp - extraction - wood chips - large | regulation ability | cold start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0022
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.45 | biomass chp - extraction - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.45 | biomass chp - extraction - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.45 | biomass chp - extraction - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.45 | biomass chp - extraction - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.45 | biomass chp - extraction - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.45 | biomass chp - extraction - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.45 | biomass chp - extraction - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.45 | biomass chp - extraction - wood chips - large | regulation ability | minimum load (of full load) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0085
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02 | biomass chp - extraction - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02 | biomass chp - extraction - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02 | biomass chp - extraction - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02 | biomass chp - extraction - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02 | biomass chp - extraction - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02 | biomass chp - extraction - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02 | biomass chp - extraction - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02 | biomass chp - extraction - wood chips - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0171
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp - extraction - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp - extraction - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp - extraction - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp - extraction - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp - extraction - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp - extraction - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp - extraction - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp - extraction - wood chips - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0012 | tk_reg | manual_category_map | PAR_0179
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2015 | 2 | biomass chp - extraction - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2020 | 2 | biomass chp - extraction - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2030 | 2 | biomass chp - extraction - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2050 | 2 | biomass chp - extraction - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2020 | 2 | biomass chp - extraction - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2050 | 2 | biomass chp - extraction - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2020 | 2 | biomass chp - extraction - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2050 | 2 | biomass chp - extraction - wood chips - large | regulation ability | warm start-up time [hours] | ELH_0012 | tk_reg | manual_category_map | PAR_0211
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.041 | biomass chp - extraction - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0012 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.041 | biomass chp - extraction - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0012 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.041 | biomass chp - extraction - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0012 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.041 | biomass chp - extraction - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0012 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.041 | biomass chp - extraction - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0012 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.041 | biomass chp - extraction - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0012 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.041 | biomass chp - extraction - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0012 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.041 | biomass chp - extraction - wood chips - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0012 | tk_tsd | manual_category_map | PAR_0003
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2015 | 0 | biomass chp - extraction - wood chips - large | technology-specific data | combustion air humidification | ELH_0012 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2020 | 0 | biomass chp - extraction - wood chips - large | technology-specific data | combustion air humidification | ELH_0012 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2030 | 0 | biomass chp - extraction - wood chips - large | technology-specific data | combustion air humidification | ELH_0012 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2050 | 0 | biomass chp - extraction - wood chips - large | technology-specific data | combustion air humidification | ELH_0012 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | lower | 2020 | 0 | biomass chp - extraction - wood chips - large | technology-specific data | combustion air humidification | ELH_0012 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | lower | 2050 | 0 | biomass chp - extraction - wood chips - large | technology-specific data | combustion air humidification | ELH_0012 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | upper | 2020 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | combustion air humidification | ELH_0012 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | upper | 2050 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | combustion air humidification | ELH_0012 | tk_tsd | manual_category_map | PAR_0025
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 32113.8561 | biomass chp - extraction - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0012 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 31369.4952 | biomass chp - extraction - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0012 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 29668.0988 | biomass chp - extraction - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0012 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 27116.0043 | biomass chp - extraction - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0012 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 28073.0397 | biomass chp - extraction - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0012 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 24670.247 | biomass chp - extraction - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0012 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 36580.0215 | biomass chp - extraction - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0012 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 36367.3469 | biomass chp - extraction - wood chips - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0012 | tk_tsd | manual_category_map | PAR_0044
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2015 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | flue gas condensation | ELH_0012 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2020 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | flue gas condensation | ELH_0012 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2030 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | flue gas condensation | ELH_0012 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2050 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | flue gas condensation | ELH_0012 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | lower | 2020 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | flue gas condensation | ELH_0012 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | lower | 2050 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | flue gas condensation | ELH_0012 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | upper | 2020 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | flue gas condensation | ELH_0012 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | upper | 2050 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | flue gas condensation | ELH_0012 | tk_tsd | manual_category_map | PAR_0062
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.021267 | biomass chp - extraction - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0012 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.021267 | biomass chp - extraction - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0012 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.021267 | biomass chp - extraction - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0012 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.021267 | biomass chp - extraction - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0012 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.021267 | biomass chp - extraction - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0012 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.021267 | biomass chp - extraction - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0012 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.021267 | biomass chp - extraction - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0012 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.021267 | biomass chp - extraction - wood chips - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0012 | tk_tsd | manual_category_map | PAR_0066
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.1697 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.1484 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.0846 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.99957 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.99957 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.93577 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.4037 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.5313 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0095
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.73373 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.71246 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.66992 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.62739 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.62739 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.58485 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.89323 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.9783 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0106
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.44662 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.43598 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.42535 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.38281 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.37218 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.35091 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.51042 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.55295 | biomass chp - extraction - wood chips - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0117
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | steam reheat | ELH_0012 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | steam reheat | ELH_0012 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | steam reheat | ELH_0012 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | steam reheat | ELH_0012 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | steam reheat | ELH_0012 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | steam reheat | ELH_0012 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | steam reheat | ELH_0012 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp - extraction - wood chips - large | technology-specific data | steam reheat | ELH_0012 | tk_tsd | manual_category_map | PAR_0197
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.1803 | biomass chp - extraction - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.1803 | biomass chp - extraction - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.1803 | biomass chp - extraction - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.1803 | biomass chp - extraction - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.1803 | biomass chp - extraction - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 1.1803 | biomass chp - extraction - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.1803 | biomass chp - extraction - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0203
ELH | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.1803 | biomass chp - extraction - wood chips - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0012 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.59 | biomass chp - extraction - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.59 | biomass chp - extraction - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.59 | biomass chp - extraction - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.52 | biomass chp - extraction - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.57 | biomass chp - extraction - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.59 | biomass chp - extraction - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.52 | biomass chp - extraction - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.53 | biomass chp - extraction - wood pellets - large | energy/technical data | cb coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0015
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5 | biomass chp - extraction - wood pellets - large | energy/technical data | construction time [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5 | biomass chp - extraction - wood pellets - large | energy/technical data | construction time [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5 | biomass chp - extraction - wood pellets - large | energy/technical data | construction time [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5 | biomass chp - extraction - wood pellets - large | energy/technical data | construction time [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 5 | biomass chp - extraction - wood pellets - large | energy/technical data | construction time [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1 | biomass chp - extraction - wood pellets - large | energy/technical data | construction time [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1 | biomass chp - extraction - wood pellets - large | energy/technical data | construction time [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1 | biomass chp - extraction - wood pellets - large | energy/technical data | construction time [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0026
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2015 | 0.17 | biomass chp - extraction - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2020 | 0.17 | biomass chp - extraction - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2030 | 0.17 | biomass chp - extraction - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2050 | 0.15 | biomass chp - extraction - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2020 | 0.17 | biomass chp - extraction - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2050 | 0.17 | biomass chp - extraction - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2020 | 0.15 | biomass chp - extraction - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2050 | 0.15 | biomass chp - extraction - wood pellets - large | energy/technical data | cv coefficient (50°c/100°c) | ELH_0013 | tk_etd | manual_category_map | PAR_0028
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.423 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.425 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.426 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.426 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.412 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.418 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.427 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.433 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0034
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.445 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.447 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.448 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.448 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.434 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.44 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.449 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.455 | biomass chp - extraction - wood pellets - large | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0013 | tk_etd | manual_category_map | PAR_0036
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | biomass chp - extraction - wood pellets - large | energy/technical data | forced outage [] | ELH_0013 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | biomass chp - extraction - wood pellets - large | energy/technical data | forced outage [] | ELH_0013 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | biomass chp - extraction - wood pellets - large | energy/technical data | forced outage [] | ELH_0013 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | biomass chp - extraction - wood pellets - large | energy/technical data | forced outage [] | ELH_0013 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03 | biomass chp - extraction - wood pellets - large | energy/technical data | forced outage [] | ELH_0013 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03 | biomass chp - extraction - wood pellets - large | energy/technical data | forced outage [] | ELH_0013 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03 | biomass chp - extraction - wood pellets - large | energy/technical data | forced outage [] | ELH_0013 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03 | biomass chp - extraction - wood pellets - large | energy/technical data | forced outage [] | ELH_0013 | tk_etd | manual_category_map | PAR_0065
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 356.4 | biomass chp - extraction - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 357.6 | biomass chp - extraction - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 358.7 | biomass chp - extraction - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 358.4 | biomass chp - extraction - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 347.3 | biomass chp - extraction - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 351.7 | biomass chp - extraction - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 359.4 | biomass chp - extraction - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 364.4 | biomass chp - extraction - wood pellets - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0071
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3 | biomass chp - extraction - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0013 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3 | biomass chp - extraction - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0013 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3 | biomass chp - extraction - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0013 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3 | biomass chp - extraction - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0013 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.6 | biomass chp - extraction - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0013 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.3 | biomass chp - extraction - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0013 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.5 | biomass chp - extraction - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0013 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.8 | biomass chp - extraction - wood pellets - large | energy/technical data | planned outage [weeks per year] | ELH_0013 | tk_etd | manual_category_map | PAR_0168
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.04 | biomass chp - extraction - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.04 | biomass chp - extraction - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.04 | biomass chp - extraction - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.04 | biomass chp - extraction - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.04 | biomass chp - extraction - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.04 | biomass chp - extraction - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.04 | biomass chp - extraction - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.04 | biomass chp - extraction - wood pellets - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0013 | tk_etd | manual_category_map | PAR_0188
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25 | biomass chp - extraction - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25 | biomass chp - extraction - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25 | biomass chp - extraction - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25 | biomass chp - extraction - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 25 | biomass chp - extraction - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 25 | biomass chp - extraction - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 25 | biomass chp - extraction - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 25 | biomass chp - extraction - wood pellets - large | energy/technical data | technical lifetime [years] | ELH_0013 | tk_etd | manual_category_map | PAR_0198
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0 | biomass chp - extraction - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0 | biomass chp - extraction - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0 | biomass chp - extraction - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0 | biomass chp - extraction - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0 | biomass chp - extraction - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0 | biomass chp - extraction - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0 | biomass chp - extraction - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0 | biomass chp - extraction - wood pellets - large | environment | ch4 [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0018
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1 | biomass chp - extraction - wood pellets - large | environment | n2o [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1 | biomass chp - extraction - wood pellets - large | environment | n2o [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1 | biomass chp - extraction - wood pellets - large | environment | n2o [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0 | biomass chp - extraction - wood pellets - large | environment | n2o [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0 | biomass chp - extraction - wood pellets - large | environment | n2o [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0 | biomass chp - extraction - wood pellets - large | environment | n2o [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 1 | biomass chp - extraction - wood pellets - large | environment | n2o [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1 | biomass chp - extraction - wood pellets - large | environment | n2o [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0089
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20 | biomass chp - extraction - wood pellets - large | environment | nox [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20 | biomass chp - extraction - wood pellets - large | environment | nox [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20 | biomass chp - extraction - wood pellets - large | environment | nox [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10 | biomass chp - extraction - wood pellets - large | environment | nox [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10 | biomass chp - extraction - wood pellets - large | environment | nox [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10 | biomass chp - extraction - wood pellets - large | environment | nox [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30 | biomass chp - extraction - wood pellets - large | environment | nox [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20 | biomass chp - extraction - wood pellets - large | environment | nox [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0152
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3 | biomass chp - extraction - wood pellets - large | environment | particles [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3 | biomass chp - extraction - wood pellets - large | environment | particles [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3 | biomass chp - extraction - wood pellets - large | environment | particles [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3 | biomass chp - extraction - wood pellets - large | environment | particles [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1 | biomass chp - extraction - wood pellets - large | environment | particles [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1 | biomass chp - extraction - wood pellets - large | environment | particles [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2 | biomass chp - extraction - wood pellets - large | environment | particles [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1 | biomass chp - extraction - wood pellets - large | environment | particles [g/gj_i] | ELH_0013 | tk_env | manual_category_map | PAR_0163
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2015 | 0.975 | biomass chp - extraction - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0013 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2020 | 0.975 | biomass chp - extraction - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0013 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2030 | 0.975 | biomass chp - extraction - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0013 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2050 | 0.975 | biomass chp - extraction - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0013 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2020 | 0.975 | biomass chp - extraction - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0013 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2050 | 0.975 | biomass chp - extraction - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0013 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2020 | 0.975 | biomass chp - extraction - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0013 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2050 | 0.975 | biomass chp - extraction - wood pellets - large | environment | so2 (degree of desulphuring) [] | ELH_0013 | tk_env | manual_category_map | PAR_0181
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 60612.2449 | biomass chp - extraction - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0013 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 58485.4995 | biomass chp - extraction - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0013 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 55295.3813 | biomass chp - extraction - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0013 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 52105.2632 | biomass chp - extraction - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0013 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 54232.0086 | biomass chp - extraction - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0013 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 48915.145 | biomass chp - extraction - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0013 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 66992.4812 | biomass chp - extraction - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0013 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 66992.4812 | biomass chp - extraction - wood pellets - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0013 | tk_fin | manual_category_map | PAR_0042
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.3607 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.2863 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.1693 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.0204 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.0523 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.9141 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 2.7541 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 2.9562 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0093
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.4249 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.3824 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.3079 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.2335 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.2335 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.1484 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.6801 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.8077 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0104
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0.93577 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0.9145 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0.86133 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.7869 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0.8188 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.75499 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.0634 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.1484 | biomass chp - extraction - wood pellets - large | financial data | nominal investment (installation) [meur/mw_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0115
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 1.1697 | biomass chp - extraction - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 1.1697 | biomass chp - extraction - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 1.1697 | biomass chp - extraction - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 1.1697 | biomass chp - extraction - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.276 | biomass chp - extraction - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.276 | biomass chp - extraction - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 1.1697 | biomass chp - extraction - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 1.1697 | biomass chp - extraction - wood pellets - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0013 | tk_fin | manual_category_map | PAR_0201
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 12 | biomass chp - extraction - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 12 | biomass chp - extraction - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 12 | biomass chp - extraction - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 12 | biomass chp - extraction - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2020 | 12 | biomass chp - extraction - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2050 | 12 | biomass chp - extraction - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2020 | 12 | biomass chp - extraction - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2050 | 12 | biomass chp - extraction - wood pellets - large | regulation ability | cold start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0022
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.15 | biomass chp - extraction - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.15 | biomass chp - extraction - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.15 | biomass chp - extraction - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.15 | biomass chp - extraction - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.15 | biomass chp - extraction - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.15 | biomass chp - extraction - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.15 | biomass chp - extraction - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.15 | biomass chp - extraction - wood pellets - large | regulation ability | minimum load (of full load) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0085
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02 | biomass chp - extraction - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02 | biomass chp - extraction - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02 | biomass chp - extraction - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02 | biomass chp - extraction - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02 | biomass chp - extraction - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02 | biomass chp - extraction - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02 | biomass chp - extraction - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02 | biomass chp - extraction - wood pellets - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0171
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04 | biomass chp - extraction - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04 | biomass chp - extraction - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04 | biomass chp - extraction - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04 | biomass chp - extraction - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04 | biomass chp - extraction - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04 | biomass chp - extraction - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04 | biomass chp - extraction - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04 | biomass chp - extraction - wood pellets - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0013 | tk_reg | manual_category_map | PAR_0179
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 2 | biomass chp - extraction - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 2 | biomass chp - extraction - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 2 | biomass chp - extraction - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 2 | biomass chp - extraction - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 2 | biomass chp - extraction - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 2 | biomass chp - extraction - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 2 | biomass chp - extraction - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 2 | biomass chp - extraction - wood pellets - large | regulation ability | warm start-up time [hours] | ELH_0013 | tk_reg | manual_category_map | PAR_0211
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.036 | biomass chp - extraction - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0013 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.036 | biomass chp - extraction - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0013 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.036 | biomass chp - extraction - wood pellets - large | technology-specific data | additional heat potential with heat pumps (of thermal input) [] | ELH_0013 | tk_tsd | manual_category_map | PAR_0003
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2015 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | combustion air humidification | ELH_0013 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2020 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | combustion air humidification | ELH_0013 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2030 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | combustion air humidification | ELH_0013 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2050 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | combustion air humidification | ELH_0013 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | lower | 2020 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | combustion air humidification | ELH_0013 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | lower | 2050 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | combustion air humidification | ELH_0013 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | upper | 2020 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | combustion air humidification | ELH_0013 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | upper | 2050 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | combustion air humidification | ELH_0013 | tk_tsd | manual_category_map | PAR_0025
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 26796.9925 | biomass chp - extraction - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0013 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 26158.9689 | biomass chp - extraction - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0013 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 24989.2589 | biomass chp - extraction - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0013 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 23287.8625 | biomass chp - extraction - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0013 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 23606.8743 | biomass chp - extraction - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0013 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 21267.4544 | biomass chp - extraction - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0013 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 30093.4479 | biomass chp - extraction - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0013 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 30412.4597 | biomass chp - extraction - wood pellets - large | technology-specific data | fixed o&m (*total) [eur/mw_i/y] | ELH_0013 | tk_tsd | manual_category_map | PAR_0044
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2015 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | flue gas condensation | ELH_0013 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2020 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | flue gas condensation | ELH_0013 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2030 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | flue gas condensation | ELH_0013 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2050 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | flue gas condensation | ELH_0013 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | lower | 2020 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | flue gas condensation | ELH_0013 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | lower | 2050 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | flue gas condensation | ELH_0013 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | upper | 2020 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | flue gas condensation | ELH_0013 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | upper | 2050 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | flue gas condensation | ELH_0013 | tk_tsd | manual_category_map | PAR_0062
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0013 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0013 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0013 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0013 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0013 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0013 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0013 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0 | biomass chp - extraction - wood pellets - large | technology-specific data | fuel storage specific cost in excess of 2 days [meur/mw_i/storage day] | ELH_0013 | tk_tsd | manual_category_map | PAR_0066
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0527 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.0208 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.9783 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.90387 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.89323 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.84006 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.2335 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.3398 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (*total) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0095
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.62739 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.61676 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.58485 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.55295 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.51042 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.75499 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.8188 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (equipment) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0106
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.41472 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.40408 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.38281 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.35091 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.35091 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.32965 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.47852 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.52105 | biomass chp - extraction - wood pellets - large | technology-specific data | nominal investment (installation) [meur/mw_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0117
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | steam reheat | ELH_0013 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | steam reheat | ELH_0013 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | steam reheat | ELH_0013 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | steam reheat | ELH_0013 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | steam reheat | ELH_0013 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | steam reheat | ELH_0013 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | steam reheat | ELH_0013 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1 | biomass chp - extraction - wood pellets - large | technology-specific data | steam reheat | ELH_0013 | tk_tsd | manual_category_map | PAR_0197
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0203
ELH | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.54232 | biomass chp - extraction - wood pellets - large | technology-specific data | variable o&m (*total) [eur/mwh_i] | ELH_0013 | tk_tsd | manual_category_map | PAR_0203
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Construction time [years] | years |  | B | 1 | ctrl | 2015 | 0.4 | stirling engine - back pressure - biomass - medium | energy/technical data | construction time [years] | ELH_0070 | tk_etd | manual_category_map | PAR_0026
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Construction time [years] | years |  | B | 1 | ctrl | 2020 | 0.3 | stirling engine - back pressure - biomass - medium | energy/technical data | construction time [years] | ELH_0070 | tk_etd | manual_category_map | PAR_0026
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 1 | ctrl | 2015 | 0.2 | stirling engine - back pressure - biomass - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0070 | tk_etd | manual_category_map | PAR_0036
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 1 | ctrl | 2020 | 0.22 | stirling engine - back pressure - biomass - medium | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0070 | tk_etd | manual_category_map | PAR_0036
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.04 | stirling engine - back pressure - biomass - medium | energy/technical data | forced outage [] | ELH_0070 | tk_etd | manual_category_map | PAR_0065
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.03 | stirling engine - back pressure - biomass - medium | energy/technical data | forced outage [] | ELH_0070 | tk_etd | manual_category_map | PAR_0065
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 1 | ctrl | 2015 | 0.04 | stirling engine - back pressure - biomass - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0070 | tk_etd | manual_category_map | PAR_0071
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 1 | ctrl | 2020 | 0.04 | stirling engine - back pressure - biomass - medium | energy/technical data | generating capacity for one unit [mw_e] | ELH_0070 | tk_etd | manual_category_map | PAR_0071
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2015 | 3 | stirling engine - back pressure - biomass - medium | energy/technical data | planned outage [weeks per year] | ELH_0070 | tk_etd | manual_category_map | PAR_0168
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2020 | 2 | stirling engine - back pressure - biomass - medium | energy/technical data | planned outage [weeks per year] | ELH_0070 | tk_etd | manual_category_map | PAR_0168
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 15 | stirling engine - back pressure - biomass - medium | energy/technical data | technical lifetime [years] | ELH_0070 | tk_etd | manual_category_map | PAR_0198
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 15 | stirling engine - back pressure - biomass - medium | energy/technical data | technical lifetime [years] | ELH_0070 | tk_etd | manual_category_map | PAR_0198
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | CH4 [ppm] | ppm |  |  | 1 | ctrl | 2015 | 0 | stirling engine - back pressure - biomass - medium | environment | ch4 [ppm] | ELH_0070 | tk_env | manual_category_map | PAR_0019
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | CH4 [ppm] | ppm |  |  | 1 | ctrl | 2020 | 0 | stirling engine - back pressure - biomass - medium | environment | ch4 [ppm] | ELH_0070 | tk_env | manual_category_map | PAR_0019
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | N2O [ppm] | ppm |  |  | 1 | ctrl | 2015 | 0 | stirling engine - back pressure - biomass - medium | environment | n2o [ppm] | ELH_0070 | tk_env | manual_category_map | PAR_0090
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | N2O [ppm] | ppm |  |  | 1 | ctrl | 2020 | 0 | stirling engine - back pressure - biomass - medium | environment | n2o [ppm] | ELH_0070 | tk_env | manual_category_map | PAR_0090
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | NOX [ppm] | ppm |  |  | 1 | ctrl | 2015 | 130 | stirling engine - back pressure - biomass - medium | environment | nox [ppm] | ELH_0070 | tk_env | manual_category_map | PAR_0154
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | NOX [ppm] | ppm |  |  | 1 | ctrl | 2020 | 100 | stirling engine - back pressure - biomass - medium | environment | nox [ppm] | ELH_0070 | tk_env | manual_category_map | PAR_0154
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  | 1 | ctrl | 2015 | 0 | stirling engine - back pressure - biomass - medium | environment | so2 (degree of desulphuring) [] | ELH_0070 | tk_env | manual_category_map | PAR_0181
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  | 1 | ctrl | 2020 | 0 | stirling engine - back pressure - biomass - medium | environment | so2 (degree of desulphuring) [] | ELH_0070 | tk_env | manual_category_map | PAR_0181
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, E] | 1 | ctrl | 2015 | 34027.927 | stirling engine - back pressure - biomass - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0070 | tk_fin | manual_category_map | PAR_0042
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, E] | 1 | ctrl | 2020 | 34027.927 | stirling engine - back pressure - biomass - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0070 | tk_fin | manual_category_map | PAR_0042
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, E] | 1 | ctrl | 2030 | 0 | stirling engine - back pressure - biomass - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0070 | tk_fin | manual_category_map | PAR_0042
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, E] | 1 | ctrl | 2050 | 0 | stirling engine - back pressure - biomass - medium | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0070 | tk_fin | manual_category_map | PAR_0042
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 1 | ctrl | 2015 | 5.3169 | stirling engine - back pressure - biomass - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0070 | tk_fin | manual_category_map | PAR_0093
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 1 | ctrl | 2020 | 4.0408 | stirling engine - back pressure - biomass - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0070 | tk_fin | manual_category_map | PAR_0093
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 1 | ctrl | 2030 | 0 | stirling engine - back pressure - biomass - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0070 | tk_fin | manual_category_map | PAR_0093
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 1 | ctrl | 2050 | 0 | stirling engine - back pressure - biomass - medium | financial data | nominal investment (*total) [meur/mw_e] | ELH_0070 | tk_fin | manual_category_map | PAR_0093
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [D, E] | 1 | ctrl | 2015 | 27.6477 | stirling engine - back pressure - biomass - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0070 | tk_fin | manual_category_map | PAR_0201
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [D, E] | 1 | ctrl | 2020 | 22.3308 | stirling engine - back pressure - biomass - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0070 | tk_fin | manual_category_map | PAR_0201
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [D, E] | 1 | ctrl | 2030 | 0 | stirling engine - back pressure - biomass - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0070 | tk_fin | manual_category_map | PAR_0201
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [D, E] | 1 | ctrl | 2050 | 0 | stirling engine - back pressure - biomass - medium | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0070 | tk_fin | manual_category_map | PAR_0201
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 1 | stirling engine - back pressure - biomass - medium | regulation ability | cold start-up time [hours] | ELH_0070 | tk_reg | manual_category_map | PAR_0022
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 1 | stirling engine - back pressure - biomass - medium | regulation ability | cold start-up time [hours] | ELH_0070 | tk_reg | manual_category_map | PAR_0022
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Technology-specific data | Generating capacity for one unit [MW_h] | MW_h |  |  | 1 | ctrl | 2015 | 0.12 | stirling engine - back pressure - biomass - medium | technology-specific data | generating capacity for one unit [mw_h] | ELH_0070 | tk_tsd | manual_category_map | PAR_0072
ELH | 10 Stirling | Stirling engine - back pressure - biomass - medium | Technology-specific data | Generating capacity for one unit [MW_h] | MW_h |  |  | 1 | ctrl | 2020 | 0.12 | stirling engine - back pressure - biomass - medium | technology-specific data | generating capacity for one unit [mw_h] | ELH_0070 | tk_tsd | manual_category_map | PAR_0072
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [C, L] | [, *, *, *] | ctrl | 2020 | 1.67 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0069 | tk_etd | manual_category_map | PAR_0015
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [C, L] | [, *, *, *] | ctrl | 2030 | 1.61 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0069 | tk_etd | manual_category_map | PAR_0015
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [C, L] | [, *, *, *] | ctrl | 2050 | 1.61 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0069 | tk_etd | manual_category_map | PAR_0015
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 1 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0069 | tk_etd | manual_category_map | PAR_0026
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0069 | tk_etd | manual_category_map | PAR_0026
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0069 | tk_etd | manual_category_map | PAR_0026
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | construction time [years] | ELH_0069 | tk_etd | manual_category_map | PAR_0026
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | ctrl | 2015 | 0.56 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0034
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | ctrl | 2020 | 0.58 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0034
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | ctrl | 2030 | 0.6 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0034
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | ctrl | 2050 | 0.6 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0034
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | lower | 2020 | 0.52 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0034
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | lower | 2050 | 0.56 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0034
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | upper | 2020 | 0.6 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0034
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | upper | 2050 | 0.62 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0034
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  |  | ctrl | 2015 | 0.56 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0036
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  |  | ctrl | 2020 | 0.58 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0036
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  |  | ctrl | 2030 | 0.6 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0036
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  |  | ctrl | 2050 | 0.6 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0069 | tk_etd | manual_category_map | PAR_0036
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | [3, *, *, *] | ctrl | 2015 | 0.25 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0069 | tk_etd | manual_category_map | PAR_0071
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | [3, *, *, *] | ctrl | 2020 | 2.5 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0069 | tk_etd | manual_category_map | PAR_0071
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | [3, *, *, *] | ctrl | 2030 | 10 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0069 | tk_etd | manual_category_map | PAR_0071
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | [3, *, *, *] | ctrl | 2050 | 20 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0069 | tk_etd | manual_category_map | PAR_0071
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [6, 6, *, *] | ctrl | 2015 | 15 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0069 | tk_etd | manual_category_map | PAR_0198
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [6, 6, *, *] | ctrl | 2020 | 20 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0069 | tk_etd | manual_category_map | PAR_0198
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [6, 6, *, *] | ctrl | 2030 | 20 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0069 | tk_etd | manual_category_map | PAR_0198
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [6, 6, *, *] | ctrl | 2050 | 20 | solid oxide fuel cell - back pressure - biogas - small | energy/technical data | technical lifetime [years] | ELH_0069 | tk_etd | manual_category_map | PAR_0198
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 7 | ctrl | 2015 | 1.25 | solid oxide fuel cell - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0069 | tk_env | manual_category_map | PAR_0018
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 7 | ctrl | 2020 | 1.25 | solid oxide fuel cell - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0069 | tk_env | manual_category_map | PAR_0018
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 7 | ctrl | 2030 | 1.25 | solid oxide fuel cell - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0069 | tk_env | manual_category_map | PAR_0018
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 7 | ctrl | 2050 | 1.25 | solid oxide fuel cell - back pressure - biogas - small | environment | ch4 [g/gj_i] | ELH_0069 | tk_env | manual_category_map | PAR_0018
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2015 | 1.3 | solid oxide fuel cell - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0069 | tk_env | manual_category_map | PAR_0152
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 1.4 | solid oxide fuel cell - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0069 | tk_env | manual_category_map | PAR_0152
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 1.5 | solid oxide fuel cell - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0069 | tk_env | manual_category_map | PAR_0152
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 1.6 | solid oxide fuel cell - back pressure - biogas - small | environment | nox [g/gj_i] | ELH_0069 | tk_env | manual_category_map | PAR_0152
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 3 | ctrl | 2015 | 1 | solid oxide fuel cell - back pressure - biogas - small | environment | so2 (degree of desulphuring) [] | ELH_0069 | tk_env | manual_category_map | PAR_0181
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 3 | ctrl | 2020 | 1 | solid oxide fuel cell - back pressure - biogas - small | environment | so2 (degree of desulphuring) [] | ELH_0069 | tk_env | manual_category_map | PAR_0181
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 3 | ctrl | 2030 | 1 | solid oxide fuel cell - back pressure - biogas - small | environment | so2 (degree of desulphuring) [] | ELH_0069 | tk_env | manual_category_map | PAR_0181
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 3 | ctrl | 2050 | 1 | solid oxide fuel cell - back pressure - biogas - small | environment | so2 (degree of desulphuring) [] | ELH_0069 | tk_env | manual_category_map | PAR_0181
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | ctrl | 2015 | 441299.678 | solid oxide fuel cell - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0069 | tk_fin | manual_category_map | PAR_0042
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | ctrl | 2020 | 175456.4985 | solid oxide fuel cell - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0069 | tk_fin | manual_category_map | PAR_0042
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | ctrl | 2030 | 106337.2718 | solid oxide fuel cell - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0069 | tk_fin | manual_category_map | PAR_0042
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | ctrl | 2050 | 42534.9087 | solid oxide fuel cell - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0069 | tk_fin | manual_category_map | PAR_0042
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | lower | 2020 | 143555.3169 | solid oxide fuel cell - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0069 | tk_fin | manual_category_map | PAR_0042
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | lower | 2050 | 21267.4544 | solid oxide fuel cell - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0069 | tk_fin | manual_category_map | PAR_0042
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | upper | 2020 | 308378.0882 | solid oxide fuel cell - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0069 | tk_fin | manual_category_map | PAR_0042
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | upper | 2050 | 69119.2267 | solid oxide fuel cell - back pressure - biogas - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0069 | tk_fin | manual_category_map | PAR_0042
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | ctrl | 2015 | 8.826 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0093
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | ctrl | 2020 | 3.5091 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0093
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | ctrl | 2030 | 2.1267 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0093
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | ctrl | 2050 | 0.8507 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0093
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | lower | 2020 | 2.8711 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0093
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | lower | 2050 | 0.42535 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0093
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | upper | 2020 | 6.1676 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0093
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | upper | 2050 | 1.3824 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0093
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2015 | 7.0608 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0104
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2020 | 2.4564 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0104
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 1.276 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0104
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.48915 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0104
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0104
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0104
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0104
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0104
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2015 | 1.7652 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0115
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2020 | 1.0527 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0115
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.8507 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0115
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.36155 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0115
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0115
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0115
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0115
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0115
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2015 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | startup cost [eur/mw_e/startup] | ELH_0069 | tk_fin | manual_category_map | PAR_0195
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | startup cost [eur/mw_e/startup] | ELH_0069 | tk_fin | manual_category_map | PAR_0195
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2030 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | startup cost [eur/mw_e/startup] | ELH_0069 | tk_fin | manual_category_map | PAR_0195
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | startup cost [eur/mw_e/startup] | ELH_0069 | tk_fin | manual_category_map | PAR_0195
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | lower | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | startup cost [eur/mw_e/startup] | ELH_0069 | tk_fin | manual_category_map | PAR_0195
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | lower | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | startup cost [eur/mw_e/startup] | ELH_0069 | tk_fin | manual_category_map | PAR_0195
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | upper | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | startup cost [eur/mw_e/startup] | ELH_0069 | tk_fin | manual_category_map | PAR_0195
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | upper | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | startup cost [eur/mw_e/startup] | ELH_0069 | tk_fin | manual_category_map | PAR_0195
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2015 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0201
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0201
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2030 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0201
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0201
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0201
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0201
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2020 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0201
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2050 | 0 | solid oxide fuel cell - back pressure - biogas - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0069 | tk_fin | manual_category_map | PAR_0201
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [*, *, *, *] | ctrl | 2015 | 25 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0069 | tk_reg | manual_category_map | PAR_0022
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [*, *, *, *] | ctrl | 2020 | 25 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0069 | tk_reg | manual_category_map | PAR_0022
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [*, *, *, *] | ctrl | 2030 | 25 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0069 | tk_reg | manual_category_map | PAR_0022
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [*, *, *, *] | ctrl | 2050 | 25 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | cold start-up time [hours] | ELH_0069 | tk_reg | manual_category_map | PAR_0022
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.7 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0069 | tk_reg | manual_category_map | PAR_0085
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.7 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0069 | tk_reg | manual_category_map | PAR_0085
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.7 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0069 | tk_reg | manual_category_map | PAR_0085
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.7 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | minimum load (of full load) [] | ELH_0069 | tk_reg | manual_category_map | PAR_0085
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | E |  | ctrl | 2015 | 0.03 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0069 | tk_reg | manual_category_map | PAR_0211
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | E |  | ctrl | 2020 | 0.03 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0069 | tk_reg | manual_category_map | PAR_0211
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | E |  | ctrl | 2030 | 0.03 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0069 | tk_reg | manual_category_map | PAR_0211
ELH | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | E |  | ctrl | 2050 | 0.03 | solid oxide fuel cell - back pressure - biogas - small | regulation ability | warm start-up time [hours] | ELH_0069 | tk_reg | manual_category_map | PAR_0211
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | D |  | ctrl | 2020 | 1.25 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0050 | tk_etd | manual_category_map | PAR_0015
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | D |  | ctrl | 2030 | 1.25 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0050 | tk_etd | manual_category_map | PAR_0015
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | D |  | ctrl | 2050 | 1.25 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | cb coefficient (50°c/100°c) | ELH_0050 | tk_etd | manual_category_map | PAR_0015
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | construction time [years] | ELH_0050 | tk_etd | manual_category_map | PAR_0026
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | construction time [years] | ELH_0050 | tk_etd | manual_category_map | PAR_0026
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | construction time [years] | ELH_0050 | tk_etd | manual_category_map | PAR_0026
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | construction time [years] | ELH_0050 | tk_etd | manual_category_map | PAR_0026
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | ctrl | 2015 | 0.45 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0034
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | ctrl | 2020 | 0.5 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0034
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | ctrl | 2030 | 0.5 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0034
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | ctrl | 2050 | 0.5 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0034
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | lower | 2020 | 0.45 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0034
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | lower | 2050 | 0.46 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0034
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | upper | 2020 | 0.52 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0034
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | upper | 2050 | 0.53 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, annual average) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0034
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2015 | 0.45 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0036
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2020 | 0.5 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0036
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2030 | 0.5 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0036
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2050 | 0.5 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | electrical efficiency (net, name plate) [] | ELH_0050 | tk_etd | manual_category_map | PAR_0036
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.001 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | forced outage [] | ELH_0050 | tk_etd | manual_category_map | PAR_0065
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.001 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | forced outage [] | ELH_0050 | tk_etd | manual_category_map | PAR_0065
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.001 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | forced outage [] | ELH_0050 | tk_etd | manual_category_map | PAR_0065
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.001 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | forced outage [] | ELH_0050 | tk_etd | manual_category_map | PAR_0065
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 5 | ctrl | 2015 | 0.05 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0050 | tk_etd | manual_category_map | PAR_0071
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 5 | ctrl | 2020 | 0.1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0050 | tk_etd | manual_category_map | PAR_0071
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 5 | ctrl | 2030 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0050 | tk_etd | manual_category_map | PAR_0071
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 5 | ctrl | 2050 | 2 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0050 | tk_etd | manual_category_map | PAR_0071
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 0.1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | planned outage [weeks per year] | ELH_0050 | tk_etd | manual_category_map | PAR_0168
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 0.1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | planned outage [weeks per year] | ELH_0050 | tk_etd | manual_category_map | PAR_0168
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 0.1 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | planned outage [weeks per year] | ELH_0050 | tk_etd | manual_category_map | PAR_0168
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2015 | 10 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | technical lifetime [years] | ELH_0050 | tk_etd | manual_category_map | PAR_0198
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 10 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | technical lifetime [years] | ELH_0050 | tk_etd | manual_category_map | PAR_0198
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 10 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | technical lifetime [years] | ELH_0050 | tk_etd | manual_category_map | PAR_0198
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 10 | low temp pem fuel cell - back pressure - hydrogen - small | energy/technical data | technical lifetime [years] | ELH_0050 | tk_etd | manual_category_map | PAR_0198
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | ch4 [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0018
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | ch4 [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0018
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | ch4 [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0018
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | ch4 [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0018
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | n2o [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0089
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | n2o [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0089
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | n2o [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0089
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | n2o [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0089
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | nox [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0152
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | nox [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0152
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | nox [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0152
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | environment | nox [g/gj_i] | ELH_0050 | tk_env | manual_category_map | PAR_0152
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | environment | so2 (degree of desulphuring) [] | ELH_0050 | tk_env | manual_category_map | PAR_0181
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | environment | so2 (degree of desulphuring) [] | ELH_0050 | tk_env | manual_category_map | PAR_0181
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | environment | so2 (degree of desulphuring) [] | ELH_0050 | tk_env | manual_category_map | PAR_0181
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 1 | low temp pem fuel cell - back pressure - hydrogen - small | environment | so2 (degree of desulphuring) [] | ELH_0050 | tk_env | manual_category_map | PAR_0181
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | ctrl | 2015 | 101020.4082 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0050 | tk_fin | manual_category_map | PAR_0042
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | ctrl | 2020 | 69119.2267 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0050 | tk_fin | manual_category_map | PAR_0042
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | ctrl | 2030 | 58485.4995 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0050 | tk_fin | manual_category_map | PAR_0042
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | ctrl | 2050 | 42534.9087 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0050 | tk_fin | manual_category_map | PAR_0042
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | lower | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0050 | tk_fin | manual_category_map | PAR_0042
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | lower | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0050 | tk_fin | manual_category_map | PAR_0042
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | upper | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0050 | tk_fin | manual_category_map | PAR_0042
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | upper | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0050 | tk_fin | manual_category_map | PAR_0042
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | ctrl | 2015 | 2.0204 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0093
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | ctrl | 2020 | 1.3824 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0093
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | ctrl | 2030 | 1.1697 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0093
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | ctrl | 2050 | 0.8507 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0093
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | lower | 2020 | 1.1697 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0093
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | lower | 2050 | 0.53169 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0093
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | upper | 2020 | 1.7014 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0093
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | upper | 2050 | 0.95704 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0093
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2015 | 1.7014 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0104
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2020 | 1.0634 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0104
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2030 | 0.8507 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0104
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2050 | 0.63802 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0104
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | lower | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0104
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | lower | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0104
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | upper | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0104
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | upper | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0104
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2015 | 0.31901 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0115
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2020 | 0.31901 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0115
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2030 | 0.31901 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0115
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2050 | 0.21267 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0115
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | lower | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0115
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | lower | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0115
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | upper | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0115
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | upper | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0115
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2015 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0201
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0201
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2030 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0201
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0201
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0201
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0201
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2020 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0201
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2050 | 0 | low temp pem fuel cell - back pressure - hydrogen - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0050 | tk_fin | manual_category_map | PAR_0201
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.1 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | minimum load (of full load) [] | ELH_0050 | tk_reg | manual_category_map | PAR_0085
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.1 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | minimum load (of full load) [] | ELH_0050 | tk_reg | manual_category_map | PAR_0085
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.1 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | minimum load (of full load) [] | ELH_0050 | tk_reg | manual_category_map | PAR_0085
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.1 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | minimum load (of full load) [] | ELH_0050 | tk_reg | manual_category_map | PAR_0085
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.5 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0050 | tk_reg | manual_category_map | PAR_0171
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.25 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0050 | tk_reg | manual_category_map | PAR_0171
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.025 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0050 | tk_reg | manual_category_map | PAR_0171
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.0125 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0050 | tk_reg | manual_category_map | PAR_0171
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.01 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | warm start-up time [hours] | ELH_0050 | tk_reg | manual_category_map | PAR_0211
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.01 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | warm start-up time [hours] | ELH_0050 | tk_reg | manual_category_map | PAR_0211
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.01 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | warm start-up time [hours] | ELH_0050 | tk_reg | manual_category_map | PAR_0211
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.01 | low temp pem fuel cell - back pressure - hydrogen - small | regulation ability | warm start-up time [hours] | ELH_0050 | tk_reg | manual_category_map | PAR_0211
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Technology-specific data | Minimum load efficiency [] |  |  |  | 5 | ctrl | 2015 | 0.3 | low temp pem fuel cell - back pressure - hydrogen - small | technology-specific data | minimum load efficiency [] | ELH_0050 | tk_tsd | manual_category_map | PAR_0087
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Technology-specific data | Minimum load efficiency [] |  |  |  | 5 | ctrl | 2020 | 0.35 | low temp pem fuel cell - back pressure - hydrogen - small | technology-specific data | minimum load efficiency [] | ELH_0050 | tk_tsd | manual_category_map | PAR_0087
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Technology-specific data | Minimum load efficiency [] |  |  |  | 5 | ctrl | 2030 | 0.35 | low temp pem fuel cell - back pressure - hydrogen - small | technology-specific data | minimum load efficiency [] | ELH_0050 | tk_tsd | manual_category_map | PAR_0087
ELH | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Technology-specific data | Minimum load efficiency [] |  |  |  | 5 | ctrl | 2050 | 0.35 | low temp pem fuel cell - back pressure - hydrogen - small | technology-specific data | minimum load efficiency [] | ELH_0050 | tk_tsd | manual_category_map | PAR_0087
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | ctrl | 2020 | 1.5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | ctrl | 2025 | 1.5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | ctrl | 2030 | 1.5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | ctrl | 2040 | 1.5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | ctrl | 2050 | 1.5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | lower | 2020 | 1 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | lower | 2050 | 1 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | upper | 2020 | 3 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 18 | upper | 2050 | 3 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | construction time [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | ctrl | 2020 | 0.025 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | ctrl | 2025 | 0.025 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | ctrl | 2030 | 0.02 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | ctrl | 2040 | 0.018 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | ctrl | 2050 | 0.015 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | lower | 2020 | 0.01 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | lower | 2050 | 0.01 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | upper | 2020 | 0.05 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [%] | pct. |  | B | 18 | upper | 2050 | 0.05 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | forced outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0064
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | ctrl | 2020 | 4.2 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | ctrl | 2025 | 4.5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | ctrl | 2030 | 5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | ctrl | 2040 | 5.5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | ctrl | 2050 | 6 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | lower | 2020 | 2 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | lower | 2050 | 1.5 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | upper | 2020 | 6 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 2 | upper | 2050 | 8 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | generating capacity for one unit [mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | ctrl | 2020 | 0.003 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | ctrl | 2025 | 0.003 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | ctrl | 2030 | 0.003 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | ctrl | 2040 | 0.003 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | ctrl | 2050 | 0.003 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | lower | 2020 | 0.001 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | lower | 2050 | 0.001 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | upper | 2020 | 0.005 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [%] | pct. |  | C | 18 | upper | 2050 | 0.005 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | planned outage [%] | ELH_0056 | tk_etd | manual_category_map | PAR_0167
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | ctrl | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | ctrl | 2025 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | ctrl | 2030 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | ctrl | 2040 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | ctrl | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | lower | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | lower | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | upper | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F |  | upper | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0056 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | ctrl | 2020 | 27 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | ctrl | 2025 | 27 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | ctrl | 2030 | 30 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | ctrl | 2040 | 30 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | ctrl | 2050 | 30 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | lower | 2020 | 25 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | lower | 2050 | 25 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | upper | 2020 | 35 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 11 | upper | 2050 | 40 | onshore wind turbine, utility - renewable power - wind - large | energy/technical data | technical lifetime [years] | ELH_0056 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | ctrl | 2020 | 16396.953 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | ctrl | 2025 | 17386.6339 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | ctrl | 2030 | 16662.668 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | ctrl | 2040 | 15965.3648 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | ctrl | 2050 | 15602.0693 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | lower | 2020 | 13117.5624 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | lower | 2050 | 12481.6554 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | upper | 2020 | 19676.3436 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [J, N] | [20, 21] | upper | 2050 | 18722.4831 | onshore wind turbine, utility - renewable power - wind - large | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0056 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | ctrl | 2020 | 1.1055 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | ctrl | 2025 | 1.1846 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | ctrl | 2030 | 1.1466 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | ctrl | 2040 | 1.1097 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | ctrl | 2050 | 1.0903 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | lower | 2020 | 0.87223 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | lower | 2050 | 0.79557 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | upper | 2020 | 1.3083 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [I, M] | [12, 1, 18] | upper | 2050 | 1.1934 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (*total) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2020 | 0.034864 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2025 | 0.031588 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2030 | 0.031588 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2040 | 0.031588 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2050 | 0.031588 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | lower | 2020 | 0.027891 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | lower | 2050 | 0.02527 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | upper | 2020 | 0.041836 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | upper | 2050 | 0.037905 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (decommissioning of existing turbines) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0101
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2020 | 0.7823 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2025 | 0.86408 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2030 | 0.8281 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2040 | 0.79345 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2050 | 0.77539 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | lower | 2020 | 0.62584 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | lower | 2050 | 0.62032 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | upper | 2020 | 0.93876 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | upper | 2050 | 0.93047 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | ctrl | 2020 | 0.016945 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | ctrl | 2025 | 0.01744 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | ctrl | 2030 | 0.017078 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | ctrl | 2040 | 0.016723 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | ctrl | 2050 | 0.016534 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | lower | 2020 | 0.013556 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | lower | 2050 | 0.013227 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | upper | 2020 | 0.020334 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | O | 20 | upper | 2050 | 0.019841 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0109
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2020 | 0.08809 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2025 | 0.089515 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2030 | 0.085788 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2040 | 0.082198 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | ctrl | 2050 | 0.080327 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | lower | 2020 | 0.070472 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | lower | 2050 | 0.064262 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | upper | 2020 | 0.10571 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation/development) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 20 | upper | 2050 | 0.096393 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (installation/development) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0120
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | ctrl | 2020 | 0.10649 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | ctrl | 2025 | 0.11096 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | ctrl | 2030 | 0.11096 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | ctrl | 2040 | 0.11096 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | ctrl | 2050 | 0.11096 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | lower | 2020 | 0.085193 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | lower | 2050 | 0.088766 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | upper | 2020 | 0.12779 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land purchase/rent) [MEUR/MW_e] | MEUR/MW_e | 2020 | P | 20 | upper | 2050 | 0.13315 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (land purchase/rent) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0124
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | ctrl | 2020 | 0.076821 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | ctrl | 2025 | 0.070163 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | ctrl | 2030 | 0.071124 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | ctrl | 2040 | 0.072104 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | ctrl | 2050 | 0.072637 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | lower | 2020 | 0.061457 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | lower | 2050 | 0.05811 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | upper | 2020 | 0.092185 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (purchase of neighbour settlements) [MEUR/MW_e] | MEUR/MW_e | 2020 | [Q] | [20, 21] | upper | 2050 | 0.087165 | onshore wind turbine, utility - renewable power - wind - large | financial data | nominal investment (purchase of neighbour settlements) [meur/mw_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0131
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | ctrl | 2020 | 2.1133 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | ctrl | 2025 | 2.061 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | ctrl | 2030 | 1.9752 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | ctrl | 2040 | 1.8925 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | ctrl | 2050 | 1.8495 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | lower | 2020 | 1.6906 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | lower | 2050 | 1.4796 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | upper | 2020 | 2.5359 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [J, N] | [13, 21] | upper | 2050 | 2.2194 | onshore wind turbine, utility - renewable power - wind - large | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0056 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | ctrl | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | ctrl | 2025 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | ctrl | 2030 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | ctrl | 2040 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | ctrl | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | lower | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | lower | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | upper | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G |  | upper | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | primary regulation (of full load, per 30 seconds) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0171
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2025 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2030 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2040 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | lower | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | lower | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | upper | 2020 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | upper | 2050 | - | onshore wind turbine, utility - renewable power - wind - large | regulation ability | secondary regulation (of full load, per minute) [] | ELH_0056 | tk_reg | manual_category_map | PAR_0179
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | ctrl | 2020 | 0.972 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | ctrl | 2025 | 0.97 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | ctrl | 2030 | 0.977 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | ctrl | 2040 | 0.977 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | ctrl | 2050 | 0.982 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | lower | 2020 | 0.989 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | lower | 2050 | 0.989 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | upper | 2020 | 0.945 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [%] | pct. |  |  | [18, 21] | upper | 2050 | 0.945 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | availability [%] | ELH_0056 | tk_tsd | manual_category_map | PAR_0006
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | ctrl | 2020 | 3400 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | ctrl | 2025 | 3500 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | ctrl | 2030 | 3600 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | ctrl | 2040 | 3700 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | ctrl | 2050 | 3800 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | lower | 2020 | 2000 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | lower | 2050 | 2000 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | upper | 2020 | 4000 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 2 | upper | 2050 | 4500 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0056 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | ctrl | 2020 | 0.38813 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | ctrl | 2025 | 0.39954 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | ctrl | 2030 | 0.41096 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | ctrl | 2040 | 0.42237 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | ctrl | 2050 | 0.43379 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | lower | 2020 | 0.22831 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | lower | 2050 | 0.22831 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | upper | 2020 | 0.45662 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [18, 21] | upper | 2050 | 0.5137 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | average capacity factor [] | ELH_0056 | tk_tsd | manual_category_map | PAR_0013
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | ctrl | 2020 | 85 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | ctrl | 2025 | 90 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | ctrl | 2030 | 100 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | ctrl | 2040 | 105 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | ctrl | 2050 | 110 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | lower | 2020 | 85 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | lower | 2050 | 85 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | upper | 2020 | 120 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [18, 21] | upper | 2050 | 150 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | hub height [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | ctrl | 2020 | 130 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | ctrl | 2025 | 135 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | ctrl | 2030 | 145 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | ctrl | 2040 | 155 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | ctrl | 2050 | 165 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | lower | 2020 | 90 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | lower | 2050 | 100 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | upper | 2020 | 130 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [18, 21] | upper | 2050 | 150 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | rotor diameter [m] | ELH_0056 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2020 | 316.4264 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2025 | 310 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2030 | 302.7918 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2040 | 291.4804 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2050 | 280.6038 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | lower | 2020 | 314.3801 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | lower | 2050 | 190.9859 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | upper | 2020 | 452.0377 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | upper | 2050 | 452.7074 | onshore wind turbine, utility - renewable power - wind - large | technology-specific data | specific power [w_e/m2] | ELH_0056 | tk_tsd | manual_category_map | PAR_0194
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 1 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | construction time [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | construction time [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | construction time [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | construction time [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2020 | 0.5 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | construction time [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2050 | 0.5 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | construction time [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2020 | 1.5 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | construction time [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2050 | 1.5 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | construction time [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0026
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | forced outage [] | ELH_0055 | tk_etd | manual_category_map | PAR_0065
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | forced outage [] | ELH_0055 | tk_etd | manual_category_map | PAR_0065
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | forced outage [] | ELH_0055 | tk_etd | manual_category_map | PAR_0065
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | forced outage [] | ELH_0055 | tk_etd | manual_category_map | PAR_0065
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.02 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | forced outage [] | ELH_0055 | tk_etd | manual_category_map | PAR_0065
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.02 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | forced outage [] | ELH_0055 | tk_etd | manual_category_map | PAR_0065
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.1 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | forced outage [] | ELH_0055 | tk_etd | manual_category_map | PAR_0065
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.1 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | forced outage [] | ELH_0055 | tk_etd | manual_category_map | PAR_0065
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 0.01 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 0.01 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 0.01 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2050 | 0.01 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 0 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 0 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 0.03 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 0.03 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | generating capacity for one unit [mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0071
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2015 | 0.16 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | planned outage [weeks per year] | ELH_0055 | tk_etd | manual_category_map | PAR_0168
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2020 | 0.16 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | planned outage [weeks per year] | ELH_0055 | tk_etd | manual_category_map | PAR_0168
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.16 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | planned outage [weeks per year] | ELH_0055 | tk_etd | manual_category_map | PAR_0168
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2050 | 0.16 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | planned outage [weeks per year] | ELH_0055 | tk_etd | manual_category_map | PAR_0168
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2020 | 0.05 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | planned outage [weeks per year] | ELH_0055 | tk_etd | manual_category_map | PAR_0168
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2050 | 0.05 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | planned outage [weeks per year] | ELH_0055 | tk_etd | manual_category_map | PAR_0168
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2020 | 0.26 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | planned outage [weeks per year] | ELH_0055 | tk_etd | manual_category_map | PAR_0168
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2050 | 0.26 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | planned outage [weeks per year] | ELH_0055 | tk_etd | manual_category_map | PAR_0168
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | C |  | ctrl | 2015 | 0.8 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | C |  | ctrl | 2020 | 0.8 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | C |  | ctrl | 2030 | 0.8 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | C |  | ctrl | 2050 | 0.8 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0055 | tk_etd | manual_category_map | PAR_0188
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 20 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | technical lifetime [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 20 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | technical lifetime [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 20 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | technical lifetime [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 20 | onshore wind turbine, residential - renewable power - wind - small | energy/technical data | technical lifetime [years] | ELH_0055 | tk_etd | manual_category_map | PAR_0198
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | ctrl | 2015 | 106337.2718 | onshore wind turbine, residential - renewable power - wind - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0055 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | ctrl | 2020 | 101020.4082 | onshore wind turbine, residential - renewable power - wind - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0055 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | ctrl | 2030 | 95703.5446 | onshore wind turbine, residential - renewable power - wind - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0055 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | ctrl | 2050 | 90386.681 | onshore wind turbine, residential - renewable power - wind - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0055 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | lower | 2020 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0055 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | lower | 2050 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0055 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | upper | 2020 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0055 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | upper | 2050 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0055 | tk_fin | manual_category_map | PAR_0042
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2015 | 4.2535 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2020 | 4.0408 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2030 | 3.8388 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2050 | 3.6474 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2020 | 3.1901 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2050 | 3.1901 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2020 | 6.3802 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2050 | 6.3802 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (*total) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0093
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2015 | 0.95704 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2020 | 0.95704 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2030 | 0.95704 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2050 | 0.95704 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2020 | 0.90387 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2050 | 0.90387 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2020 | 1.0102 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2050 | 1.0102 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (equipment) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0104
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2015 | 0.10634 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0115
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2020 | 0.10634 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0115
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2030 | 0.10634 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0115
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2050 | 0.10634 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0115
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2020 | 0.15951 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0115
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2050 | 0.15951 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0115
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2020 | 0.053169 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0115
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2050 | 0.053169 | onshore wind turbine, residential - renewable power - wind - small | financial data | nominal investment (installation) [meur/mw_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0115
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2015 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2020 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2030 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2050 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2020 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2050 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2020 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2050 | 0 | onshore wind turbine, residential - renewable power - wind - small | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0055 | tk_fin | manual_category_map | PAR_0201
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | ctrl | 2015 | 1600 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0055 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | ctrl | 2020 | 1800 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0055 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | ctrl | 2030 | 2000 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0055 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | ctrl | 2050 | 2200 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0055 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | lower | 2020 | 1000 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0055 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | lower | 2050 | 1000 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0055 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | upper | 2020 | 2300 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0055 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | upper | 2050 | 2300 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0055 | tk_tsd | manual_category_map | PAR_0010
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | ctrl | 2015 | 540 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | fixed o&m (*total) [eur/unit/y] | ELH_0055 | tk_tsd | manual_category_map | PAR_0046
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | ctrl | 2020 | 540 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | fixed o&m (*total) [eur/unit/y] | ELH_0055 | tk_tsd | manual_category_map | PAR_0046
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | ctrl | 2030 | 540 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | fixed o&m (*total) [eur/unit/y] | ELH_0055 | tk_tsd | manual_category_map | PAR_0046
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | ctrl | 2050 | 540 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | fixed o&m (*total) [eur/unit/y] | ELH_0055 | tk_tsd | manual_category_map | PAR_0046
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | lower | 2020 | 350 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | fixed o&m (*total) [eur/unit/y] | ELH_0055 | tk_tsd | manual_category_map | PAR_0046
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | lower | 2050 | 350 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | fixed o&m (*total) [eur/unit/y] | ELH_0055 | tk_tsd | manual_category_map | PAR_0046
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | upper | 2020 | 700 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | fixed o&m (*total) [eur/unit/y] | ELH_0055 | tk_tsd | manual_category_map | PAR_0046
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | upper | 2050 | 700 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | fixed o&m (*total) [eur/unit/y] | ELH_0055 | tk_tsd | manual_category_map | PAR_0046
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | ctrl | 2015 | 18 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | hub height [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | ctrl | 2020 | 18 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | hub height [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | ctrl | 2030 | 18 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | hub height [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | ctrl | 2050 | 18 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | hub height [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | lower | 2020 | 14 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | hub height [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | lower | 2050 | 14 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | hub height [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | upper | 2020 | 18 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | hub height [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | upper | 2050 | 18 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | hub height [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0080
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | ctrl | 2015 | 8 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | rotor diameter [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | ctrl | 2020 | 11 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | rotor diameter [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | ctrl | 2030 | 12 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | rotor diameter [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | ctrl | 2050 | 14 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | rotor diameter [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | lower | 2020 | 4 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | rotor diameter [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | lower | 2050 | 4 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | rotor diameter [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | upper | 2020 | 14 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | rotor diameter [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0175
ELH | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | upper | 2050 | 14 | onshore wind turbine, residential - renewable power - wind - small | technology-specific data | rotor diameter [m] | ELH_0055 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2025 | 3.5 | nearshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0051 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2030 | 3.5 | nearshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0051 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | lower | 2025 | 3 | nearshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0051 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | upper | 2025 | 4 | nearshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0051 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2025 | 0.02 | nearshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0051 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2030 | 0.02 | nearshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0051 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2025 | 0.02 | nearshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0051 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2025 | 0.02 | nearshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0051 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2025 | 15 | nearshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0051 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2030 | 20 | nearshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0051 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | lower | 2025 | 15 | nearshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0051 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | upper | 2025 | 15 | nearshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0051 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2025 | 0.5 | nearshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0051 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.5 | nearshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0051 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2025 | 0.5 | nearshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0051 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2025 | 0.5 | nearshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0051 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2025 | 200 | nearshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0051 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2030 | 166.6667 | nearshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0051 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | lower | 2025 | 222.2222 | nearshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0051 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | upper | 2025 | 181.8182 | nearshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0051 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2025 | 30 | nearshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0051 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2030 | 30 | nearshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0051 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2025 | 25 | nearshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0051 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2025 | 40 | nearshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0051 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2025 | 44000 | nearshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0051 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2030 | 34000 | nearshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0051 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | lower | 2025 | 39600 | nearshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0051 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | upper | 2025 | 48400 | nearshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0051 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 1.9153 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 1.5411 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 1.7237 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 2.1068 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 0.017652 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.016835 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 0.015887 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 0.019417 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2025 | 0.088261 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.088261 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2025 | 0.079435 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2025 | 0.097087 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 0.48544 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.37914 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 0.43689 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 0.53398 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 0.13239 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.12626 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 0.11915 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 0.14563 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2025 | 0 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2025 | 0 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2025 | 0 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 1.1915 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.93061 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 1.0724 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 1.3107 | nearshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2025 | 4.4131 | nearshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2030 | 3.4467 | nearshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | lower | 2025 | 3.9718 | nearshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | upper | 2025 | 4.8544 | nearshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0051 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2025 | 4000 | nearshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0051 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2030 | 4150 | nearshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0051 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | lower | 2025 | 4000 | nearshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0051 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | upper | 2025 | 4000 | nearshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0051 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2025 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0051 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2030 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0051 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | lower | 2025 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0051 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | upper | 2025 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0051 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2025 | AC | nearshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0051 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2030 | AC | nearshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0051 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | lower | 2025 | AC | nearshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0051 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | upper | 2025 | AC | nearshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0051 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2025 | 150 | nearshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2030 | 170 | nearshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | lower | 2025 | 150 | nearshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | upper | 2025 | 150 | nearshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2025 | No | nearshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0051 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2030 | No | nearshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0051 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | lower | 2025 | No | nearshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0051 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | upper | 2025 | No | nearshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0051 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2025 | 236 | nearshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2030 | 280 | nearshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | lower | 2025 | 236 | nearshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | upper | 2025 | 236 | nearshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2025 | 5 | nearshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0051 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2030 | 6 | nearshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0051 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | lower | 2025 | 4.5 | nearshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0051 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | upper | 2025 | 5.5 | nearshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0051 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2025 | 343 | nearshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0051 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2030 | 320 | nearshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0051 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | lower | 2025 | 343 | nearshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0051 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | upper | 2025 | 343 | nearshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0051 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2025 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2030 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | lower | 2025 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | upper | 2025 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0051 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2025 | 20 | nearshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0051 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2030 | 20 | nearshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0051 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | lower | 2025 | 15 | nearshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0051 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Nearshore Wind AC | Nearshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | upper | 2025 | 25 | nearshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0051 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2025 | 3.5 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2030 | 3.5 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2035 | 3.5 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2040 | 3.5 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2050 | 3.5 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | lower | 2025 | 3 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | lower | 2050 | 3 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | upper | 2025 | 4 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | upper | 2050 | 4 | offshore wind - ac connected - fixed bottom | energy/technical data | construction time [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2025 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2030 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2035 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2040 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2050 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2025 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2050 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2025 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2050 | 0.02 | offshore wind - ac connected - fixed bottom | energy/technical data | forced outage [] | ELH_0052 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2025 | 15 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2030 | 20 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2035 | 25 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2040 | 30 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2050 | 35 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | lower | 2025 | 15 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | lower | 2050 | 30 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | upper | 2025 | 15 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | upper | 2050 | 40 | offshore wind - ac connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2025 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2035 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2040 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2050 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2025 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2050 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2025 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2050 | 0.5 | offshore wind - ac connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0052 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2025 | 200 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2030 | 166.6667 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2035 | 142.8571 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2040 | 125 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2050 | 100 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | lower | 2025 | 222.2222 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | lower | 2050 | 111.1111 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | upper | 2025 | 181.8182 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | upper | 2050 | 90.9091 | offshore wind - ac connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0052 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2025 | 30 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2030 | 30 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2035 | 30 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2040 | 30 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2050 | 30 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2025 | 25 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2050 | 25 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2025 | 40 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2050 | 40 | offshore wind - ac connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0052 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2025 | 44000 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2030 | 34000 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2035 | 32000 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2040 | 30000 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2050 | 28000 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | lower | 2025 | 39600 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | lower | 2050 | 18200 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | upper | 2025 | 48400 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | upper | 2050 | 37800 | offshore wind - ac connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0052 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 2.7802 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 2.3931 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 2.2482 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 2.1406 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 1.9857 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 2.5022 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 1.2907 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 3.0583 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 2.6807 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 0.044131 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.042088 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.041397 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.040965 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.040397 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 0.039718 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.026258 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 0.048544 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 0.054537 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2025 | 0.26478 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.26478 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2035 | 0.25363 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2040 | 0.24247 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.22016 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2025 | 0.23831 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0.14311 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2025 | 0.29126 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0.29722 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | ctrl | 2025 | 0.52957 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | ctrl | 2030 | 0.4136 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | ctrl | 2035 | 0.3794 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | ctrl | 2040 | 0.35919 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | ctrl | 2050 | 0.33399 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | lower | 2025 | 0.47661 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | lower | 2050 | 0.21709 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | upper | 2025 | 0.58252 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, | 1 | upper | 2050 | 0.45088 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 0.17652 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.16835 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.16559 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.16386 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.16159 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 0.15887 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.10503 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 0.19417 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 0.21815 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2025 | 0.5737 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.5737 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2035 | 0.55457 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2040 | 0.52589 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.47808 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2025 | 0.51633 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0.31075 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2025 | 0.63107 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0.64541 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 1.1915 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.93061 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.85364 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.80818 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.75147 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 1.0724 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.48846 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 1.3107 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 1.0145 | offshore wind - ac connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2025 | 4.4131 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2030 | 3.4467 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2035 | 3.1616 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2040 | 2.9933 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2050 | 2.7832 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | lower | 2025 | 3.9718 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | lower | 2050 | 1.8091 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | upper | 2025 | 4.8544 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | upper | 2050 | 3.7574 | offshore wind - ac connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0052 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2025 | 4400 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2030 | 4550 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2035 | 4600 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2040 | 4650 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2050 | 4650 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | lower | 2025 | 4400 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | lower | 2050 | 4800 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | upper | 2025 | 4400 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | upper | 2050 | 4550 | offshore wind - ac connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0052 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2025 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2030 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2035 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2040 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2050 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | lower | 2025 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | lower | 2050 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | upper | 2025 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | upper | 2050 | 60 | offshore wind - ac connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0052 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2025 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2030 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2035 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2040 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2050 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | lower | 2025 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | lower | 2050 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | upper | 2025 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | upper | 2050 | AC | offshore wind - ac connected - fixed bottom | technology-specific data | grid connection type | ELH_0052 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2025 | 150 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2030 | 170 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2035 | 190 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2040 | 210 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2050 | 220 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | lower | 2025 | 150 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | lower | 2050 | 210 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | upper | 2025 | 150 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | upper | 2050 | 220 | offshore wind - ac connected - fixed bottom | technology-specific data | hub height [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2025 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2030 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2035 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2040 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2050 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | lower | 2025 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | lower | 2050 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | upper | 2025 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | upper | 2050 | Yes | offshore wind - ac connected - fixed bottom | technology-specific data | offshore substation | ELH_0052 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2025 | 236 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2030 | 280 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2035 | 320 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2040 | 350 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2050 | 380 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | lower | 2025 | 236 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | lower | 2050 | 370 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | upper | 2025 | 236 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | upper | 2050 | 390 | offshore wind - ac connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2025 | 5 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2030 | 6 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2035 | 7 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2040 | 8 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2050 | 10 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | lower | 2025 | 4.5 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | lower | 2050 | 9 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | upper | 2025 | 5.5 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | upper | 2050 | 11 | offshore wind - ac connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2025 | 343 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2030 | 320 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2035 | 310 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2040 | 310 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2050 | 310 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | lower | 2025 | 343 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | lower | 2050 | 280 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | upper | 2025 | 343 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | upper | 2050 | 340 | offshore wind - ac connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0052 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2025 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2030 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2035 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2040 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2050 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | lower | 2025 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | lower | 2050 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | upper | 2025 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | upper | 2050 | 30 | offshore wind - ac connected - fixed bottom | technology-specific data | water depth [m] | ELH_0052 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2025 | 70 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2030 | 70 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2035 | 70 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2040 | 70 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2050 | 70 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | lower | 2025 | 65 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | lower | 2050 | 65 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | upper | 2025 | 75 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Fixed | Offshore Wind - AC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | upper | 2050 | 75 | offshore wind - ac connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0052 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2030 | 3.5 | offshore wind - ac connected - floating | energy/technical data | construction time [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2035 | 3.5 | offshore wind - ac connected - floating | energy/technical data | construction time [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2040 | 3.5 | offshore wind - ac connected - floating | energy/technical data | construction time [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2050 | 3.5 | offshore wind - ac connected - floating | energy/technical data | construction time [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | lower | 2050 | 3 | offshore wind - ac connected - floating | energy/technical data | construction time [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | upper | 2050 | 4 | offshore wind - ac connected - floating | energy/technical data | construction time [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2030 | 0.02 | offshore wind - ac connected - floating | energy/technical data | forced outage [] | ELH_0053 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2035 | 0.02 | offshore wind - ac connected - floating | energy/technical data | forced outage [] | ELH_0053 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2040 | 0.02 | offshore wind - ac connected - floating | energy/technical data | forced outage [] | ELH_0053 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2050 | 0.02 | offshore wind - ac connected - floating | energy/technical data | forced outage [] | ELH_0053 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2050 | 0.02 | offshore wind - ac connected - floating | energy/technical data | forced outage [] | ELH_0053 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2050 | 0.02 | offshore wind - ac connected - floating | energy/technical data | forced outage [] | ELH_0053 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2030 | 20 | offshore wind - ac connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2035 | 25 | offshore wind - ac connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2040 | 30 | offshore wind - ac connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2050 | 35 | offshore wind - ac connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | lower | 2050 | 30 | offshore wind - ac connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | upper | 2050 | 40 | offshore wind - ac connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.5 | offshore wind - ac connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0053 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2035 | 0.5 | offshore wind - ac connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0053 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2040 | 0.5 | offshore wind - ac connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0053 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2050 | 0.5 | offshore wind - ac connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0053 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2050 | 0.5 | offshore wind - ac connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0053 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2050 | 0.5 | offshore wind - ac connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0053 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2030 | 166.6667 | offshore wind - ac connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2035 | 142.8571 | offshore wind - ac connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2040 | 125 | offshore wind - ac connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2050 | 100 | offshore wind - ac connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | lower | 2050 | 111.1111 | offshore wind - ac connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | upper | 2050 | 90.9091 | offshore wind - ac connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0053 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2030 | 30 | offshore wind - ac connected - floating | energy/technical data | technical lifetime [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2035 | 30 | offshore wind - ac connected - floating | energy/technical data | technical lifetime [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2040 | 30 | offshore wind - ac connected - floating | energy/technical data | technical lifetime [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2050 | 30 | offshore wind - ac connected - floating | energy/technical data | technical lifetime [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2050 | 25 | offshore wind - ac connected - floating | energy/technical data | technical lifetime [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2050 | 40 | offshore wind - ac connected - floating | energy/technical data | technical lifetime [years] | ELH_0053 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | ctrl | 2030 | 62000 | offshore wind - ac connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0053 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | ctrl | 2035 | 42000 | offshore wind - ac connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0053 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | ctrl | 2040 | 33000 | offshore wind - ac connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0053 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | ctrl | 2050 | 28000 | offshore wind - ac connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0053 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | lower | 2050 | 14000 | offshore wind - ac connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0053 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | upper | 2050 | 37800 | offshore wind - ac connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0053 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 3.5581 | offshore wind - ac connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 2.9 | offshore wind - ac connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 2.495 | offshore wind - ac connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 2.2536 | offshore wind - ac connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 1.3636 | offshore wind - ac connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 3.1437 | offshore wind - ac connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.042088 | offshore wind - ac connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.041397 | offshore wind - ac connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.040965 | offshore wind - ac connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.040397 | offshore wind - ac connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.026258 | offshore wind - ac connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 0.054537 | offshore wind - ac connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.17652 | offshore wind - ac connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2035 | 0.16909 | offshore wind - ac connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2040 | 0.16165 | offshore wind - ac connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.14678 | offshore wind - ac connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0.095404 | offshore wind - ac connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0.19815 | offshore wind - ac connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | ctrl | 2030 | 1.6037 | offshore wind - ac connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | ctrl | 2035 | 1.0536 | offshore wind - ac connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | ctrl | 2040 | 0.79448 | offshore wind - ac connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | ctrl | 2050 | 0.67531 | offshore wind - ac connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | lower | 2050 | 0.33766 | offshore wind - ac connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | upper | 2050 | 1.013 | offshore wind - ac connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.23148 | offshore wind - ac connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.22768 | offshore wind - ac connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.16386 | offshore wind - ac connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.16159 | offshore wind - ac connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.10503 | offshore wind - ac connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 0.21815 | offshore wind - ac connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.5737 | offshore wind - ac connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2035 | 0.55457 | offshore wind - ac connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2040 | 0.52589 | offshore wind - ac connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.47808 | offshore wind - ac connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0.31075 | offshore wind - ac connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0.64541 | offshore wind - ac connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.93061 | offshore wind - ac connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.85364 | offshore wind - ac connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.80818 | offshore wind - ac connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.75147 | offshore wind - ac connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.48846 | offshore wind - ac connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 1.0145 | offshore wind - ac connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | ctrl | 2030 | 6.2184 | offshore wind - ac connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | ctrl | 2035 | 4.2108 | offshore wind - ac connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | ctrl | 2040 | 3.2403 | offshore wind - ac connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | ctrl | 2050 | 2.7867 | offshore wind - ac connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | lower | 2050 | 1.3933 | offshore wind - ac connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | upper | 2050 | 4.18 | offshore wind - ac connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0053 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2030 | 4150 | offshore wind - ac connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0053 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2035 | 4200 | offshore wind - ac connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0053 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2040 | 4250 | offshore wind - ac connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0053 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2050 | 4250 | offshore wind - ac connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0053 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | lower | 2050 | 4400 | offshore wind - ac connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0053 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | upper | 2050 | 4150 | offshore wind - ac connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0053 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2030 | 35 | offshore wind - ac connected - floating | technology-specific data | distance to shore [km] | ELH_0053 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2035 | 35 | offshore wind - ac connected - floating | technology-specific data | distance to shore [km] | ELH_0053 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2040 | 35 | offshore wind - ac connected - floating | technology-specific data | distance to shore [km] | ELH_0053 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2050 | 35 | offshore wind - ac connected - floating | technology-specific data | distance to shore [km] | ELH_0053 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | lower | 2050 | 35 | offshore wind - ac connected - floating | technology-specific data | distance to shore [km] | ELH_0053 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | upper | 2050 | 35 | offshore wind - ac connected - floating | technology-specific data | distance to shore [km] | ELH_0053 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2030 | AC | offshore wind - ac connected - floating | technology-specific data | grid connection type | ELH_0053 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2035 | AC | offshore wind - ac connected - floating | technology-specific data | grid connection type | ELH_0053 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2040 | AC | offshore wind - ac connected - floating | technology-specific data | grid connection type | ELH_0053 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2050 | AC | offshore wind - ac connected - floating | technology-specific data | grid connection type | ELH_0053 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | lower | 2050 | AC | offshore wind - ac connected - floating | technology-specific data | grid connection type | ELH_0053 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | upper | 2050 | AC | offshore wind - ac connected - floating | technology-specific data | grid connection type | ELH_0053 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2030 | 170 | offshore wind - ac connected - floating | technology-specific data | hub height [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2035 | 190 | offshore wind - ac connected - floating | technology-specific data | hub height [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2040 | 210 | offshore wind - ac connected - floating | technology-specific data | hub height [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2050 | 220 | offshore wind - ac connected - floating | technology-specific data | hub height [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | lower | 2050 | 210 | offshore wind - ac connected - floating | technology-specific data | hub height [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | upper | 2050 | 220 | offshore wind - ac connected - floating | technology-specific data | hub height [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2030 | Yes | offshore wind - ac connected - floating | technology-specific data | offshore substation | ELH_0053 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2035 | Yes | offshore wind - ac connected - floating | technology-specific data | offshore substation | ELH_0053 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2040 | Yes | offshore wind - ac connected - floating | technology-specific data | offshore substation | ELH_0053 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2050 | Yes | offshore wind - ac connected - floating | technology-specific data | offshore substation | ELH_0053 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | lower | 2050 | Yes | offshore wind - ac connected - floating | technology-specific data | offshore substation | ELH_0053 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | upper | 2050 | Yes | offshore wind - ac connected - floating | technology-specific data | offshore substation | ELH_0053 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2030 | 280 | offshore wind - ac connected - floating | technology-specific data | rotor diameter [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2035 | 320 | offshore wind - ac connected - floating | technology-specific data | rotor diameter [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2040 | 350 | offshore wind - ac connected - floating | technology-specific data | rotor diameter [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2050 | 380 | offshore wind - ac connected - floating | technology-specific data | rotor diameter [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | lower | 2050 | 370 | offshore wind - ac connected - floating | technology-specific data | rotor diameter [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | upper | 2050 | 390 | offshore wind - ac connected - floating | technology-specific data | rotor diameter [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2030 | 6 | offshore wind - ac connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2035 | 7 | offshore wind - ac connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2040 | 8 | offshore wind - ac connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2050 | 10 | offshore wind - ac connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | lower | 2050 | 9 | offshore wind - ac connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | upper | 2050 | 11 | offshore wind - ac connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2030 | 320 | offshore wind - ac connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2035 | 310 | offshore wind - ac connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2040 | 310 | offshore wind - ac connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2050 | 310 | offshore wind - ac connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | lower | 2050 | 280 | offshore wind - ac connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | upper | 2050 | 340 | offshore wind - ac connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0053 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2030 | 75 | offshore wind - ac connected - floating | technology-specific data | water depth [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2035 | 75 | offshore wind - ac connected - floating | technology-specific data | water depth [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2040 | 75 | offshore wind - ac connected - floating | technology-specific data | water depth [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2050 | 75 | offshore wind - ac connected - floating | technology-specific data | water depth [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | lower | 2050 | 75 | offshore wind - ac connected - floating | technology-specific data | water depth [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | upper | 2050 | 75 | offshore wind - ac connected - floating | technology-specific data | water depth [m] | ELH_0053 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2030 | 70 | offshore wind - ac connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0053 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2035 | 70 | offshore wind - ac connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0053 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2040 | 70 | offshore wind - ac connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0053 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2050 | 70 | offshore wind - ac connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0053 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | lower | 2050 | 65 | offshore wind - ac connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0053 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Offshore Wind AC Floating | Offshore Wind - AC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | upper | 2050 | 75 | offshore wind - ac connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0053 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2025 | 3.5 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2030 | 3.5 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2035 | 3.5 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2040 | 3.5 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2050 | 3.5 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | lower | 2025 | 3 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | lower | 2050 | 3 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | upper | 2025 | 4 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Construction time [years] | years |  | D | 2 | upper | 2050 | 4 | far shore wind - dc connected - fixed bottom | energy/technical data | construction time [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2025 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2030 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2035 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2040 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2050 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2025 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2050 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2025 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2050 | 0.02 | far shore wind - dc connected - fixed bottom | energy/technical data | forced outage [] | ELH_0027 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2025 | 15 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2030 | 20 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2035 | 25 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2040 | 30 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2050 | 35 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | lower | 2025 | 15 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | lower | 2050 | 30 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | upper | 2025 | 15 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | upper | 2050 | 40 | far shore wind - dc connected - fixed bottom | energy/technical data | generating capacity for one unit [mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2025 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2035 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2040 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2050 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2025 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2050 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2025 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2050 | 0.5 | far shore wind - dc connected - fixed bottom | energy/technical data | planned outage [weeks per year] | ELH_0027 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2025 | 200 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2030 | 166.6667 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2035 | 142.8571 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2040 | 125 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2050 | 100 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | lower | 2025 | 222.2222 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | lower | 2050 | 111.1111 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | upper | 2025 | 181.8182 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | upper | 2050 | 90.9091 | far shore wind - dc connected - fixed bottom | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0027 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2025 | 30 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2030 | 30 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2035 | 30 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2040 | 30 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2050 | 30 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2025 | 25 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2050 | 25 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2025 | 40 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2050 | 40 | far shore wind - dc connected - fixed bottom | energy/technical data | technical lifetime [years] | ELH_0027 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2025 | 44000 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2030 | 34000 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2035 | 32000 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2040 | 30000 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | ctrl | 2050 | 28000 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | lower | 2025 | 39600 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | lower | 2050 | 18200 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | upper | 2025 | 48400 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, F | 2 | upper | 2050 | 37800 | far shore wind - dc connected - fixed bottom | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0027 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 3.6187 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 3.222 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 3.0318 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 2.8978 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 2.6836 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 3.2568 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 1.7444 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 3.9806 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 3.6229 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (*total) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 0.044131 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.042088 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.041397 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.040965 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.040397 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 0.039718 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.026258 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 0.048544 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 0.054537 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2025 | 0.5737 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.5737 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2035 | 0.55054 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2040 | 0.52559 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.47749 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2025 | 0.51633 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0.31037 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2025 | 0.63107 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0.64461 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | ctrl | 2025 | 0.5737 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | ctrl | 2030 | 0.44807 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | ctrl | 2035 | 0.41101 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | ctrl | 2040 | 0.38913 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | ctrl | 2050 | 0.36182 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | lower | 2025 | 0.51633 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | lower | 2050 | 0.23518 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | upper | 2025 | 0.63107 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A | 1 | upper | 2050 | 0.48846 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 0.17652 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.16835 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.16559 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.16386 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.16159 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 0.15887 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.10503 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 0.19417 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 0.21815 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2025 | 1.0591 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 1.0591 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2035 | 1.0096 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2040 | 0.97005 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.89086 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2025 | 0.95322 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0.57906 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2025 | 1.165 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 1.2027 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (substation) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2025 | 1.1915 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.93061 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.85364 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.80818 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.75147 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2025 | 1.0724 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.48846 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2025 | 1.3107 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 1.0145 | far shore wind - dc connected - fixed bottom | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2025 | 4.4131 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2030 | 3.4467 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2035 | 3.1616 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2040 | 2.9933 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | ctrl | 2050 | 2.7832 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | lower | 2025 | 3.9718 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | lower | 2050 | 1.8091 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | upper | 2025 | 4.8544 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, F | 2 | upper | 2050 | 3.7574 | far shore wind - dc connected - fixed bottom | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0027 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2025 | 4500 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2030 | 4650 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2035 | 4700 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2040 | 4750 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2050 | 4750 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | lower | 2025 | 4500 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | lower | 2050 | 4900 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | upper | 2025 | 4500 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | upper | 2050 | 4650 | far shore wind - dc connected - fixed bottom | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0027 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2025 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2030 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2035 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2040 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2050 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | lower | 2025 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | lower | 2050 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | upper | 2025 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Distance to shore [km] | km |  | A |  | upper | 2050 | 175 | far shore wind - dc connected - fixed bottom | technology-specific data | distance to shore [km] | ELH_0027 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2025 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2030 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2035 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2040 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2050 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | lower | 2025 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | lower | 2050 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | upper | 2025 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Grid connection type |  |  | A |  | upper | 2050 | DC | far shore wind - dc connected - fixed bottom | technology-specific data | grid connection type | ELH_0027 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2025 | 150 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2030 | 170 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2035 | 190 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2040 | 210 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2050 | 220 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | lower | 2025 | 150 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | lower | 2050 | 210 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | upper | 2025 | 150 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Hub height [m] | m |  | A | 3 | upper | 2050 | 220 | far shore wind - dc connected - fixed bottom | technology-specific data | hub height [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2025 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2030 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2035 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2040 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2050 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | lower | 2025 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | lower | 2050 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | upper | 2025 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Offshore substation |  |  | A |  | upper | 2050 | Yes | far shore wind - dc connected - fixed bottom | technology-specific data | offshore substation | ELH_0027 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2025 | 236 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2030 | 280 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2035 | 320 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2040 | 350 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2050 | 380 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | lower | 2025 | 236 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | lower | 2050 | 370 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | upper | 2025 | 236 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | upper | 2050 | 390 | far shore wind - dc connected - fixed bottom | technology-specific data | rotor diameter [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2025 | 5 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2030 | 6 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2035 | 7 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2040 | 8 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2050 | 10 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | lower | 2025 | 4.5 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | lower | 2050 | 9 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | upper | 2025 | 5.5 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | upper | 2050 | 11 | far shore wind - dc connected - fixed bottom | technology-specific data | specific area coverage [mw_e/km2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2025 | 343 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2030 | 320 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2035 | 310 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2040 | 310 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2050 | 310 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | lower | 2025 | 343 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | lower | 2050 | 280 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | upper | 2025 | 343 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | upper | 2050 | 340 | far shore wind - dc connected - fixed bottom | technology-specific data | specific power [w_e/m2] | ELH_0027 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2025 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2030 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2035 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2040 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2050 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | lower | 2025 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | lower | 2050 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | upper | 2025 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Water depth [m] | m |  | A |  | upper | 2050 | 40 | far shore wind - dc connected - fixed bottom | technology-specific data | water depth [m] | ELH_0027 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2025 | 70 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2030 | 70 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2035 | 70 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2040 | 70 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2050 | 70 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | lower | 2025 | 65 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | lower | 2050 | 65 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | upper | 2025 | 75 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Fixed | Far shore Wind - DC connected - Fixed bottom | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | upper | 2050 | 75 | far shore wind - dc connected - fixed bottom | technology-specific data | wind farm size [number of turbines] | ELH_0027 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2030 | 3.5 | far shore wind - dc connected - floating | energy/technical data | construction time [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2035 | 3.5 | far shore wind - dc connected - floating | energy/technical data | construction time [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2040 | 3.5 | far shore wind - dc connected - floating | energy/technical data | construction time [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2050 | 3.5 | far shore wind - dc connected - floating | energy/technical data | construction time [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | lower | 2050 | 3 | far shore wind - dc connected - floating | energy/technical data | construction time [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Construction time [years] | years |  | D | 2 | upper | 2050 | 4 | far shore wind - dc connected - floating | energy/technical data | construction time [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0026
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2030 | 0.02 | far shore wind - dc connected - floating | energy/technical data | forced outage [] | ELH_0028 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2035 | 0.02 | far shore wind - dc connected - floating | energy/technical data | forced outage [] | ELH_0028 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2040 | 0.02 | far shore wind - dc connected - floating | energy/technical data | forced outage [] | ELH_0028 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2050 | 0.02 | far shore wind - dc connected - floating | energy/technical data | forced outage [] | ELH_0028 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2050 | 0.02 | far shore wind - dc connected - floating | energy/technical data | forced outage [] | ELH_0028 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2050 | 0.02 | far shore wind - dc connected - floating | energy/technical data | forced outage [] | ELH_0028 | tk_etd | manual_category_map | PAR_0065
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2030 | 20 | far shore wind - dc connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2035 | 25 | far shore wind - dc connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2040 | 30 | far shore wind - dc connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | ctrl | 2050 | 35 | far shore wind - dc connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | lower | 2050 | 30 | far shore wind - dc connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1 | upper | 2050 | 40 | far shore wind - dc connected - floating | energy/technical data | generating capacity for one unit [mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0071
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.5 | far shore wind - dc connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0028 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2035 | 0.5 | far shore wind - dc connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0028 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2040 | 0.5 | far shore wind - dc connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0028 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2050 | 0.5 | far shore wind - dc connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0028 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2050 | 0.5 | far shore wind - dc connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0028 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2050 | 0.5 | far shore wind - dc connected - floating | energy/technical data | planned outage [weeks per year] | ELH_0028 | tk_etd | manual_category_map | PAR_0168
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2030 | 166.6667 | far shore wind - dc connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2035 | 142.8571 | far shore wind - dc connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2040 | 125 | far shore wind - dc connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | ctrl | 2050 | 100 | far shore wind - dc connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | lower | 2050 | 111.1111 | far shore wind - dc connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E |  | upper | 2050 | 90.9091 | far shore wind - dc connected - floating | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0028 | tk_etd | manual_category_map | PAR_0188
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2030 | 30 | far shore wind - dc connected - floating | energy/technical data | technical lifetime [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2035 | 30 | far shore wind - dc connected - floating | energy/technical data | technical lifetime [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2040 | 30 | far shore wind - dc connected - floating | energy/technical data | technical lifetime [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2050 | 30 | far shore wind - dc connected - floating | energy/technical data | technical lifetime [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2050 | 25 | far shore wind - dc connected - floating | energy/technical data | technical lifetime [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2050 | 40 | far shore wind - dc connected - floating | energy/technical data | technical lifetime [years] | ELH_0028 | tk_etd | manual_category_map | PAR_0198
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | ctrl | 2030 | 62000 | far shore wind - dc connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0028 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | ctrl | 2035 | 42000 | far shore wind - dc connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0028 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | ctrl | 2040 | 33000 | far shore wind - dc connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0028 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | ctrl | 2050 | 28000 | far shore wind - dc connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0028 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | lower | 2050 | 14000 | far shore wind - dc connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0028 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | A, I, J | 2 | upper | 2050 | 42000 | far shore wind - dc connected - floating | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0028 | tk_fin | manual_category_map | PAR_0042
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 4.3525 | far shore wind - dc connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 3.6518 | far shore wind - dc connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 3.2223 | far shore wind - dc connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 2.9237 | far shore wind - dc connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 1.7991 | far shore wind - dc connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 4.0482 | far shore wind - dc connected - floating | financial data | nominal investment (*total) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0093
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.042088 | far shore wind - dc connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.041397 | far shore wind - dc connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.040965 | far shore wind - dc connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.040397 | far shore wind - dc connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.026258 | far shore wind - dc connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 0.054537 | far shore wind - dc connected - floating | financial data | nominal investment (array cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0099
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.48544 | far shore wind - dc connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2035 | 0.46584 | far shore wind - dc connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2040 | 0.44473 | far shore wind - dc connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.40403 | far shore wind - dc connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0.26262 | far shore wind - dc connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (export cables) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0.54544 | far shore wind - dc connected - floating | financial data | nominal investment (export cables) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0107
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | ctrl | 2030 | 1.6037 | far shore wind - dc connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | ctrl | 2035 | 1.0536 | far shore wind - dc connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | ctrl | 2040 | 0.79448 | far shore wind - dc connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | ctrl | 2050 | 0.67531 | far shore wind - dc connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | lower | 2050 | 0.33766 | far shore wind - dc connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, I, J | 1 | upper | 2050 | 1.013 | far shore wind - dc connected - floating | financial data | nominal investment (foundation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0108
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.23148 | far shore wind - dc connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.22768 | far shore wind - dc connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.16386 | far shore wind - dc connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.16159 | far shore wind - dc connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.10503 | far shore wind - dc connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 0.21815 | far shore wind - dc connected - floating | financial data | nominal investment (project development etc.) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0130
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 1.0591 | far shore wind - dc connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2035 | 1.0096 | far shore wind - dc connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2040 | 0.97005 | far shore wind - dc connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.89086 | far shore wind - dc connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0.57906 | far shore wind - dc connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (substation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 1.2027 | far shore wind - dc connected - floating | financial data | nominal investment (substation) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0142
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2030 | 0.93061 | far shore wind - dc connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2035 | 0.85364 | far shore wind - dc connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2040 | 0.80818 | far shore wind - dc connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | ctrl | 2050 | 0.75147 | far shore wind - dc connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | lower | 2050 | 0.48846 | far shore wind - dc connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 | A, F | 1 | upper | 2050 | 1.0145 | far shore wind - dc connected - floating | financial data | nominal investment (turbines) [meur/mw_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0150
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | ctrl | 2030 | 6.2184 | far shore wind - dc connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | ctrl | 2035 | 4.2108 | far shore wind - dc connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | ctrl | 2040 | 3.2403 | far shore wind - dc connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | ctrl | 2050 | 2.7867 | far shore wind - dc connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | lower | 2050 | 1.3933 | far shore wind - dc connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | A, I, J | 2 | upper | 2050 | 4.18 | far shore wind - dc connected - floating | financial data | variable o&m (*total) [eur/mwh_e] | ELH_0028 | tk_fin | manual_category_map | PAR_0201
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2030 | 4650 | far shore wind - dc connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0028 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2035 | 4700 | far shore wind - dc connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0028 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2040 | 4750 | far shore wind - dc connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0028 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | ctrl | 2050 | 4750 | far shore wind - dc connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0028 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | lower | 2050 | 4900 | far shore wind - dc connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0028 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A | 1 | upper | 2050 | 4650 | far shore wind - dc connected - floating | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0028 | tk_tsd | manual_category_map | PAR_0010
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2030 | 150 | far shore wind - dc connected - floating | technology-specific data | distance to shore [km] | ELH_0028 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2035 | 150 | far shore wind - dc connected - floating | technology-specific data | distance to shore [km] | ELH_0028 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2040 | 150 | far shore wind - dc connected - floating | technology-specific data | distance to shore [km] | ELH_0028 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | ctrl | 2050 | 150 | far shore wind - dc connected - floating | technology-specific data | distance to shore [km] | ELH_0028 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | lower | 2050 | 150 | far shore wind - dc connected - floating | technology-specific data | distance to shore [km] | ELH_0028 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Distance to shore [km] | km |  | A |  | upper | 2050 | 150 | far shore wind - dc connected - floating | technology-specific data | distance to shore [km] | ELH_0028 | tk_tsd | manual_category_map | PAR_0032
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2030 | DC | far shore wind - dc connected - floating | technology-specific data | grid connection type | ELH_0028 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2035 | DC | far shore wind - dc connected - floating | technology-specific data | grid connection type | ELH_0028 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2040 | DC | far shore wind - dc connected - floating | technology-specific data | grid connection type | ELH_0028 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | ctrl | 2050 | DC | far shore wind - dc connected - floating | technology-specific data | grid connection type | ELH_0028 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | lower | 2050 | DC | far shore wind - dc connected - floating | technology-specific data | grid connection type | ELH_0028 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Grid connection type |  |  | A |  | upper | 2050 | DC | far shore wind - dc connected - floating | technology-specific data | grid connection type | ELH_0028 | tk_tsd | manual_category_map | PAR_0075
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2030 | 170 | far shore wind - dc connected - floating | technology-specific data | hub height [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2035 | 190 | far shore wind - dc connected - floating | technology-specific data | hub height [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2040 | 210 | far shore wind - dc connected - floating | technology-specific data | hub height [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | ctrl | 2050 | 220 | far shore wind - dc connected - floating | technology-specific data | hub height [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | lower | 2050 | 210 | far shore wind - dc connected - floating | technology-specific data | hub height [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Hub height [m] | m |  | A | 3 | upper | 2050 | 220 | far shore wind - dc connected - floating | technology-specific data | hub height [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0080
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2030 | Yes | far shore wind - dc connected - floating | technology-specific data | offshore substation | ELH_0028 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2035 | Yes | far shore wind - dc connected - floating | technology-specific data | offshore substation | ELH_0028 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2040 | Yes | far shore wind - dc connected - floating | technology-specific data | offshore substation | ELH_0028 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | ctrl | 2050 | Yes | far shore wind - dc connected - floating | technology-specific data | offshore substation | ELH_0028 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | lower | 2050 | Yes | far shore wind - dc connected - floating | technology-specific data | offshore substation | ELH_0028 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Offshore substation |  |  | A |  | upper | 2050 | Yes | far shore wind - dc connected - floating | technology-specific data | offshore substation | ELH_0028 | tk_tsd | manual_category_map | PAR_0158
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2030 | 280 | far shore wind - dc connected - floating | technology-specific data | rotor diameter [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2035 | 320 | far shore wind - dc connected - floating | technology-specific data | rotor diameter [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2040 | 350 | far shore wind - dc connected - floating | technology-specific data | rotor diameter [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | ctrl | 2050 | 380 | far shore wind - dc connected - floating | technology-specific data | rotor diameter [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | lower | 2050 | 370 | far shore wind - dc connected - floating | technology-specific data | rotor diameter [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Rotor diameter [m] | m |  | A, H |  | upper | 2050 | 390 | far shore wind - dc connected - floating | technology-specific data | rotor diameter [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0175
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2030 | 6 | far shore wind - dc connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2035 | 7 | far shore wind - dc connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2040 | 8 | far shore wind - dc connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | ctrl | 2050 | 10 | far shore wind - dc connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | lower | 2050 | 9 | far shore wind - dc connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | A | 1 | upper | 2050 | 11 | far shore wind - dc connected - floating | technology-specific data | specific area coverage [mw_e/km2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0192
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2030 | 320 | far shore wind - dc connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2035 | 310 | far shore wind - dc connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2040 | 310 | far shore wind - dc connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | ctrl | 2050 | 310 | far shore wind - dc connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | lower | 2050 | 280 | far shore wind - dc connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | A | 2 | upper | 2050 | 340 | far shore wind - dc connected - floating | technology-specific data | specific power [w_e/m2] | ELH_0028 | tk_tsd | manual_category_map | PAR_0194
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2030 | 75 | far shore wind - dc connected - floating | technology-specific data | water depth [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2035 | 75 | far shore wind - dc connected - floating | technology-specific data | water depth [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2040 | 75 | far shore wind - dc connected - floating | technology-specific data | water depth [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | ctrl | 2050 | 75 | far shore wind - dc connected - floating | technology-specific data | water depth [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | lower | 2050 | 75 | far shore wind - dc connected - floating | technology-specific data | water depth [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Water depth [m] | m |  | A |  | upper | 2050 | 75 | far shore wind - dc connected - floating | technology-specific data | water depth [m] | ELH_0028 | tk_tsd | manual_category_map | PAR_0212
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2030 | 70 | far shore wind - dc connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0028 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2035 | 70 | far shore wind - dc connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0028 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2040 | 70 | far shore wind - dc connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0028 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | ctrl | 2050 | 70 | far shore wind - dc connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0028 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | lower | 2050 | 65 | far shore wind - dc connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0028 | tk_tsd | manual_category_map | PAR_0213
ELH | 21 Far shore Wind DC Floating | Far shore Wind - DC connected - Floating | Technology-specific data | Wind farm size [number of turbines] | numberofturbines |  | A | 1 | upper | 2050 | 75 | far shore wind - dc connected - floating | technology-specific data | wind farm size [number of turbines] | ELH_0028 | tk_tsd | manual_category_map | PAR_0213
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2035 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | construction time [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0026
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2035 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2040 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | forced outage [] | ELH_0061 | tk_etd | manual_category_map | PAR_0065
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | ctrl | 2025 | 0.006 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | ctrl | 2030 | 0.006 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | ctrl | 2035 | 0.006 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | ctrl | 2040 | 0.006 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | ctrl | 2050 | 0.006 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | lower | 2025 | 0.0051 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | lower | 2050 | 0.0051 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | upper | 2025 | 0.0075 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | C |  | upper | 2050 | 0.0078 | pv - solar - residential rooftop | energy/technical data | generating capacity for one unit [mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0071
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2030 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2035 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2040 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2025 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2050 | 0 | pv - solar - residential rooftop | energy/technical data | planned outage [weeks per year] | ELH_0061 | tk_etd | manual_category_map | PAR_0168
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | ctrl | 2025 | 4.7032 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | ctrl | 2030 | 4.5072 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | ctrl | 2035 | 4.1605 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | ctrl | 2040 | 3.8633 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | ctrl | 2050 | 3.4895 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | lower | 2025 | 3.9977 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | lower | 2050 | 2.9661 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | upper | 2025 | 5.879 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | X,B3 | 6 | upper | 2050 | 4.5363 | pv - solar - residential rooftop | energy/technical data | space requirement [1000 m2/mw_e] | ELH_0061 | tk_etd | manual_category_map | PAR_0188
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2025 | 40 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 40 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2035 | 40 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2040 | 40 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 40 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | lower | 2025 | 34 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | lower | 2050 | 34 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | upper | 2025 | 50 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | upper | 2050 | 52 | pv - solar - residential rooftop | energy/technical data | technical lifetime [years] | ELH_0061 | tk_etd | manual_category_map | PAR_0198
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | ctrl | 2025 | 4790 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | ctrl | 2030 | 4680 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | ctrl | 2035 | 4590 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | ctrl | 2040 | 4530 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | ctrl | 2050 | 4480 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | lower | 2025 | 4070 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | lower | 2050 | 3810 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | upper | 2025 | 5990 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2025 | P |  | upper | 2050 | 5830 | pv - solar - residential rooftop | financial data | fixed o&m (*total) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0042
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | ctrl | 2025 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | ctrl | 2030 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | ctrl | 2035 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | ctrl | 2040 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | ctrl | 2050 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | lower | 2025 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | lower | 2050 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | upper | 2025 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2025 |  |  | upper | 2050 | 0 | pv - solar - residential rooftop | financial data | fixed o&m (land rent) [eur/mw_e/y] | ELH_0061 | tk_fin | manual_category_map | PAR_0054
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2025 | 0.9503 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2030 | 0.86931 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2035 | 0.80566 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2040 | 0.75606 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2050 | 0.69552 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | lower | 2025 | 0.80775 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | lower | 2050 | 0.59119 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | upper | 2025 | 1.1879 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O | 6,7,8,9,10,12 | upper | 2050 | 0.90417 | pv - solar - residential rooftop | financial data | nominal investment (*total) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0093
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | ctrl | 2025 | 0.90505 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | ctrl | 2030 | 0.82792 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | ctrl | 2035 | 0.76729 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | ctrl | 2040 | 0.72005 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | ctrl | 2050 | 0.6624 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | lower | 2025 | 0.76929 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | lower | 2050 | 0.56304 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | upper | 2025 | 1.1313 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,N | 6,7,8,9,10 | upper | 2050 | 0.86112 | pv - solar - residential rooftop | financial data | nominal investment (*total, per dc) [meur/mwp] | ELH_0061 | tk_fin | manual_category_map | PAR_0097
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | ctrl | 2025 | 0.028525 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | ctrl | 2030 | 0.027602 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | ctrl | 2035 | 0.026243 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | ctrl | 2040 | 0.025033 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | ctrl | 2050 | 0.02328 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | lower | 2025 | 0.024247 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | lower | 2050 | 0.019788 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | upper | 2025 | 0.035657 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2025 | AA |  | upper | 2050 | 0.030264 | pv - solar - residential rooftop | financial data | nominal investment (grid connection) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0109
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2025 | 0.30008 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2030 | 0.29037 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2035 | 0.27607 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2040 | 0.26334 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2050 | 0.2449 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | lower | 2025 | 0.25507 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | lower | 2050 | 0.20816 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | upper | 2025 | 0.3751 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | upper | 2050 | 0.31837 | pv - solar - residential rooftop | financial data | nominal investment (installation) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0115
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2025 | 0.1155 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2030 | 0.098062 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2035 | 0.087544 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2040 | 0.08011 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2050 | 0.072431 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | lower | 2025 | 0.098175 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | lower | 2050 | 0.061566 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | upper | 2025 | 0.14438 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | upper | 2050 | 0.09416 | pv - solar - residential rooftop | financial data | nominal investment (inverter) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0121
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2025 | 0.19826 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2030 | 0.19184 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2035 | 0.1824 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2040 | 0.17399 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2050 | 0.1618 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | lower | 2025 | 0.16852 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | lower | 2050 | 0.13753 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | upper | 2025 | 0.24782 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | upper | 2050 | 0.21034 | pv - solar - residential rooftop | financial data | nominal investment (other, i.e. residual balance of plant) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0127
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | ctrl | 2025 | 0.30794 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | ctrl | 2030 | 0.26144 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | ctrl | 2035 | 0.2334 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | ctrl | 2040 | 0.21358 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | ctrl | 2050 | 0.19311 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | lower | 2025 | 0.26175 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | lower | 2050 | 0.16414 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | upper | 2025 | 0.38492 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2025 | M,O |  | upper | 2050 | 0.25104 | pv - solar - residential rooftop | financial data | nominal investment (pv modules) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0133
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2025 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2030 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2035 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2040 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | ctrl | 2050 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | lower | 2025 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | lower | 2050 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | upper | 2025 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2025 |  |  | upper | 2050 | 0 | pv - solar - residential rooftop | financial data | nominal investment (tracker related costs) [meur/mw_e] | ELH_0061 | tk_fin | manual_category_map | PAR_0147
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | ctrl | 2025 | 0.003 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | ctrl | 2030 | 0.003 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | ctrl | 2035 | 0.003 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | ctrl | 2040 | 0.003 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | ctrl | 2050 | 0.003 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | lower | 2025 | 0.002 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | lower | 2050 | 0.002 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | upper | 2025 | 0.00375 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [%] | pct. |  |  |  | upper | 2050 | 0.0039 | pv - solar - residential rooftop | technology-specific data | average annual degradation of full-load hours [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0008
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | ctrl | 2025 | 1060 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | ctrl | 2030 | 1060 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | ctrl | 2035 | 1060 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | ctrl | 2040 | 1070 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | ctrl | 2050 | 1080 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | lower | 2025 | 900 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | lower | 2050 | 920 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | upper | 2025 | 1320 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MWp] | MWh_e/MWp |  | A1,I, K |  | upper | 2050 | 1410 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours (dc-value) [mwh_e/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0009
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | ctrl | 2025 | 1110 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | ctrl | 2030 | 1110 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | ctrl | 2035 | 1120 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | ctrl | 2040 | 1120 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | ctrl | 2050 | 1130 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | lower | 2025 | 940 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | lower | 2050 | 1020 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | upper | 2025 | 1390 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1, D |  | upper | 2050 | 1560 | pv - solar - residential rooftop | technology-specific data | average annual full-load hours [mwh_e/mw_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0010
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | ctrl | 2025 | 4560 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | ctrl | 2030 | 4460 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | ctrl | 2035 | 4370 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | ctrl | 2040 | 4310 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | ctrl | 2050 | 4270 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | lower | 2025 | 3880 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | lower | 2050 | 3630 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | upper | 2025 | 5700 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 | P |  | upper | 2050 | 5550 | pv - solar - residential rooftop | technology-specific data | fixed o&m (*total, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0052
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2030 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2035 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2040 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | lower | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | lower | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | upper | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | upper | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | fixed o&m (land rent, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0056
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2025 | 4560 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2030 | 4460 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2035 | 4370 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2040 | 4310 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | ctrl | 2050 | 4270 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | lower | 2025 | 3880 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | lower | 2050 | 3630 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | upper | 2025 | 5700 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MWp/y] | EUR/MWp/y | 2025 |  |  | upper | 2050 | 5550 | pv - solar - residential rooftop | technology-specific data | fixed o&m (other, per dc) [eur/mwp/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0057
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | ctrl | 2025 | 0.0063 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | ctrl | 2030 | 0.0063 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | ctrl | 2035 | 0.0063 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | ctrl | 2040 | 0.0063 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | ctrl | 2050 | 0.0063 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | lower | 2025 | 0.005355 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | lower | 2050 | 0.005355 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | upper | 2025 | 0.007875 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MWp] | MWp |  | J |  | upper | 2050 | 0.00819 | pv - solar - residential rooftop | technology-specific data | generating capacity for one unit (dc-value) [mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0070
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | ctrl | 2025 | 1068 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | ctrl | 2030 | 1068 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | ctrl | 2035 | 1068 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | ctrl | 2040 | 1068 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | ctrl | 2050 | 1068 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | lower | 2025 | 1000 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | lower | 2050 | 1000 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | upper | 2025 | 1100 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [kWh/m2/y] | kWh/m2/y |  | A | 1 | upper | 2050 | 1100 | pv - solar - residential rooftop | technology-specific data | global horizontal irradiance [kwh/m2/y] | ELH_0061 | tk_tsd | manual_category_map | PAR_0074
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2025 | 15 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2030 | 15 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2035 | 15 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2040 | 15 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2050 | 15 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | lower | 2025 | 12.75 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | lower | 2050 | 12.75 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | upper | 2025 | 18.75 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | upper | 2050 | 19.5 | pv - solar - residential rooftop | technology-specific data | inverter lifetime [years] | ELH_0061 | tk_tsd | manual_category_map | PAR_0082
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | ctrl | 2025 | 0.28579 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | ctrl | 2030 | 0.27654 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | ctrl | 2035 | 0.26293 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | ctrl | 2040 | 0.2508 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | ctrl | 2050 | 0.23324 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | lower | 2025 | 0.24292 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | lower | 2050 | 0.19825 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | upper | 2025 | 0.35724 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | AB |  | upper | 2050 | 0.30321 | pv - solar - residential rooftop | technology-specific data | nominal investment (installation, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0119
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2025 | 0.11 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2030 | 0.093392 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2035 | 0.083375 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2040 | 0.076295 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2050 | 0.068982 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | lower | 2025 | 0.0935 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | lower | 2050 | 0.058634 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | upper | 2025 | 0.1375 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | upper | 2050 | 0.089676 | pv - solar - residential rooftop | technology-specific data | nominal investment (inverter, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0123
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | ctrl | 2025 | 0.18882 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | ctrl | 2030 | 0.1827 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | ctrl | 2035 | 0.17371 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | ctrl | 2040 | 0.1657 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | ctrl | 2050 | 0.1541 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | lower | 2025 | 0.16049 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | lower | 2050 | 0.13098 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | upper | 2025 | 0.23602 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | Y |  | upper | 2050 | 0.20032 | pv - solar - residential rooftop | technology-specific data | nominal investment (other, i.e. residual balance of plant, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0129
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2025 | 0.29327 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2030 | 0.24899 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2035 | 0.22229 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2040 | 0.20341 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | ctrl | 2050 | 0.18391 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | lower | 2025 | 0.24928 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | lower | 2050 | 0.15633 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | upper | 2025 | 0.36659 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MWp] | MEUR/MWp | 2025 | M,O | 6,7,8,9,10,12 | upper | 2050 | 0.23909 | pv - solar - residential rooftop | technology-specific data | nominal investment (pv module, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0132
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2030 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2035 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2040 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | lower | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | lower | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | upper | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (tracker related additional cost, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | upper | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | nominal investment (tracker related additional cost, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0146
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2025 | 0.027167 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2030 | 0.026287 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2035 | 0.024994 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2040 | 0.023841 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | ctrl | 2050 | 0.022171 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | lower | 2025 | 0.023092 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | lower | 2050 | 0.018846 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | upper | 2025 | 0.033959 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MWp] | MEUR/MWp | 2025 |  |  | upper | 2050 | 0.028823 | pv - solar - residential rooftop | technology-specific data | nominal investment (transformer and grid connection, per dc) [meur/mwp] | ELH_0061 | tk_tsd | manual_category_map | PAR_0149
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | ctrl | 2025 | 0.23 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | ctrl | 2030 | 0.24 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | ctrl | 2035 | 0.26 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | ctrl | 2040 | 0.28 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | ctrl | 2050 | 0.31 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | lower | 2025 | 0.1955 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | lower | 2050 | 0.2635 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | upper | 2025 | 0.2875 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [%] | pct. |  | U, U2, M | 3,7,6 | upper | 2050 | 0.403 | pv - solar - residential rooftop | technology-specific data | pv module conversion efficiency [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0172
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | ctrl | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | ctrl | 2030 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | ctrl | 2035 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | ctrl | 2040 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | ctrl | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | lower | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | lower | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | upper | 2025 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [%] | pct. |  |  |  | upper | 2050 | 0 | pv - solar - residential rooftop | technology-specific data | performance ratio (contribution from bifaciality) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0164
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | ctrl | 2025 | 0.9 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | ctrl | 2030 | 0.9 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | ctrl | 2035 | 0.905 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | ctrl | 2040 | 0.91 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | ctrl | 2050 | 0.92 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | lower | 2025 | 0.765 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | lower | 2050 | 0.9 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | upper | 2025 | 0.92 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [%] | pct. |  | F |  | upper | 2050 | 0.94 | pv - solar - residential rooftop | technology-specific data | performance ratio (measure of combined losses) [%] | ELH_0061 | tk_tsd | manual_category_map | PAR_0165
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Sizing factor (DC/AC) [Wp/W_e] | Wp/W_e |  | D | 6 | ctrl | 2025 | 1.05 | pv - solar - residential rooftop | technology-specific data | sizing factor (dc/ac) [wp/w_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0180
ELH | 22 Rooftop PV residential | PV - solar - residential rooftop | Technology-specific data | Sizing factor (DC/AC) [Wp/W_e] | Wp/W_e |  | D | 6 | ctrl | 2030 | 1.05 | pv - solar - residential rooftop | technology-specific data | sizing factor (dc/ac) [wp/w_e] | ELH_0061 | tk_tsd | manual_category_map | PAR_0180