## Guide&Cover
Introduction
This Excel workbook is part of the "Colombian Technology Catalogue - Generation and Storage of Electricity" publication.
It provides the quantitative data in an easy-to-use manner, but should be understood in the context of the report where further descriptions are available, incl. the underlying methodology for the work.
The full report can be found at the website of the Ministry of Mines and Energy of Colombia:
https://www.minenergia.gov.co/
The full report can also be found at the website of the Danish Energy Agency in the drop-down publication list:
https://ens.dk/
Overview of the Contents
This Excel workbook contains key parameters required for conducting long-term energy modeling of Colombia’s energy system.
References and explanatory notes are provided in the main datasheet. Annotations can be found on the right-hand side of the datasheet, while detailed assumptions and reference sources are listed below the main table.
Financial projections for technologies that follow a learning curve methodology are based on learning rates and capacity forecasts from the International Energy Agency (IEA, World Energy Outlook 2023), supplemented by additional credible sources.
Disclaimer
This publication and the materials included herein are provided "as is." The authors have taken all reasonable precautions to verify the reliability of the content presented in this publication. However, neither the authoring institutions nor any of their officials, agents, data providers, third-party content providers, or licensors offer any guarantees, including but not limited to accuracy, completeness, suitability for a specific purpose, or non-infringement of third-party rights. They assume no responsibility or liability for the use of this publication or the materials contained within.
Contact information
MME: menergia@minenergia.gov.co
UPME: correspondencia@upme.gov.co
Danish Energy Agency: ens@ens.dk
Emergente: info@emergente.com.co

## Index
Intro | Technology Data for power generation and storage technologies
2.a. Residential PV (rooftop) | Version | 01
2.b. Industrial PV (rooftop) | This file contains technology data sheets related to generation of electricity and district heating. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found.
2.c. Small scale PV | Dates and descriptions of updates are listed in the ammendment sheet below.
2.d. Utility scale PV (tracking)
2.e. Floating PV | Additional information about the syntax of parameters and units in the datatabels is listed below.
3.a. Wind Onshore | Parameter structure: parameter name (extra info) (unit).
3.b. Small wind onshore | Subscript abbreviations used in the datasheets: electricity production/consumption = _e, peak capacity = _p
4.a. Wind Offshore fixed bottom
4.b. Wind offshore floating | All cost data is in | 2024 | USD
5.a. Large RoR hydro power | License:
5.b. Small RoR hydro power | This work is licensed under Attribution 4.0 International
5.c. Mini RoR hydro power
5.d. Large Hydro reservoir
6.a. Geothermal large
6.b. Geothermal small
7. Biomass power plant
8. Biogas power plant
9. Coal Supercritical
10. CCGT (GAS)
11. SCGT (GAS)
12. MSW
13.a. Nuclear PWR
13.b. Nuclear SMR
14.a. Utility-scale Lithium-ion
14.b. Small-scale Lithium-ion
15. Hydro pumped storage

## 2.a. Residential PV (rooftop)
| Technology | PV residential scale, rooftop - grid connected
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (kWe(AC)) | 6 | 6 | 6 | 2 | 20 | 2 | 20 | J | 8
| Forced outage (%) | 0 | 0 | 0 | [5 empty] | 2
| Planned outage (weeks per year) | 0 | 0 | 0 | [5 empty] | 2
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 30 | 40 |  | 2,5
| Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 |  |  |  | 5
| Space requirement (m2/kWe(AC)) | 5.1 | 4.7674 | 4.1 | 4.4 | 6 | 3.5372 | 5.1765 |  | 5
Additional data for non thermal plants
| Capacity factor (%), theoretical | 17.967 | 18.5114 | 19.6003 | 12.2944 | 25.398 | 12.7442 | 27.54 | D,E | 5
| Capacity factor (%), incl. outages | 17.967 | 18.5114 | 19.6003 | 12.2944 | 25.398 | 12.7442 | 27.54 | D,E,F | 5
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | - | - | - | -
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| CH4 (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| N2O (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
Output
| Full load hours (kWh/kW) | 1573.9051 | 1621.5992 | 1716.9874 | 1076.988 | 2224.8648 | 1116.39 | 2412.504 | D,E,K
| Peak power full load hours (kWh/kWp) | 1368.6131 | 1410.0862 | 1493.0325 | 979.08 | 1854.054 | 1014.9 | 2010.42 | D,E,F,K
Financial data
| Specific investment, total system ($M/MWe) | 1.3612 | 0.93892 | 0.63048 | 1.2861 | 1.4844 | 0.5957 | 0.68757 | A,B,C | 1,2,3,4
| Specific investment, total system, per DC ($M/MWp) | 1.1837 | 0.81645 | 0.54825 | 1.1692 | 1.237 | 0.54155 | 0.57297 | A,B,C | 1,2,3,4
| PV module cost ($/We(AC)) | 0.4749 | 0.31535 | 0.20287 | 0.44589 | 0.52285 | 0.19048 | 0.22336 | A,B,C | 1,2,3,4
| PV inverter cost ($/We(AC)) | 0.2753 | 0.18281 | 0.11761 | 0.25848 | 0.3031 | 0.11042 | 0.12948 | A,B,C | 1,2,3,4
| Balance Of Plant cost ($/We(AC)) | 0.3479 | 0.25096 | 0.17651 | 0.33084 | 0.37565 | 0.16786 | 0.19059 | A,B,C | 1,3,4
| Installation cost ($/We(AC)) | 0.2631 | 0.18979 | 0.13349 | 0.2502 | 0.28408 | 0.12694 | 0.14414 | A,B,C | 1,2,3,4
| Fixed O&M ($/MWe/year) | 17000 | 14600 | 12300 | 16700 | 17700 | 12100 | 12800 | C | 2,5,6,7,10
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1642.5 | 1642.5 | 1642.5 | 1194 | 2190 | 1194 | 2190 | I | 9,11
| DC/AC sizing factor (Wp/W) | 1.15 | 1.15 | 1.15 | 1.1 | 1.2 | 1.1 | 1.2 |  | 10
| Transposition Factor | 1.01 | 1.01 | 1.01 | 1 | 1.02 | 1 | 1.02
| Performance ratio | 0.825 | 0.85 | 0.9 | 0.82 | 0.83 | 0.85 | 0.9 | H | 2,3,10
| PV module conversion efficiency (%) | 21.5 | 23 | 25 |  |  |  |  | G | 2,3
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 2
| Average annual degradation of full-load hours (%) | 0.4 | 0.3 | 0.3 |  |  |  |  | L | 2
Financial data - per DC peak capacity
| Nominal investment (M$/MWp) | 1.1837 | 0.81645 | 0.54825 | 1.1692 | 1.237 | 0.54155 | 0.57297 | A,B,C | 1,2,3,4
| PV module cost ($/Wp(DC)) | 0.41296 | 0.27422 | 0.17641 | 0.40535 | 0.43571 | 0.17316 | 0.18613 | A,B,C | 1,2,3,4
| PV inverter cost ($/Wp(DC)) | 0.23939 | 0.15897 | 0.10227 | 0.23498 | 0.25258 | 0.10038 | 0.1079 | A,B,C | 1,2,3,4
| Balance Of Plant cost ($/Wp(DC)) | 0.30252 | 0.21823 | 0.15349 | 0.30076 | 0.31304 | 0.1526 | 0.15883 | A,B,C | 1,3,4
| Installation cost ($/Wp(DC)) | 0.22878 | 0.16504 | 0.11608 | 0.22745 | 0.23674 | 0.1154 | 0.12011 | A,B,C | 1,2,3,4
| Fixed O&M ($/MWp(DC)/year) | 14782.6087 | 12695.6522 | 10695.6522 | 13916.6667 | 16090.9091 | 10083.3333 | 11636.3636 | C | 2,5,6,7,10
| Variable O&M ($/MWh_p(DC)) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Aggregated data of Colombian projects receiving incentives/support, in alignment with further international sources
B | Cost are projected with a learning rate approach assuming a 24 % learning rate for modules and inverters based on Fraunhofer, and 20 % as per other components based on IEA, and 10 % for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
C | Uncertainty in the short term assumes the same spread as the long-term uncertainty.
D | Capacity factor = Full load hours / 8760.
E | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1643 kWh/m2/year solar irradiation mentioned here, the capacity factors should be adjusted accordingly.
F | Yearly outage time is assumed to be 0,5 % equal approximately 2 hours.
G | The efficiency is a market average of commercial modules. Modules with above 21 % efficiency are commercially available. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction (HJT) n-type mono-Si cells which both have higher efficiencies.
H | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifier, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules, which is assumed to be standard for ground-mounted plants in 2050.
I | The central value is the average annual solar irradiance received on a horizontal surface in Colombia. The areas receiving the highest levels of global solar radiation, exceeding the San Andrés and Providencia islands, large parts of the Caribbean region, and the inter-Andean valley. Minimum and maximum value correspond to The Global Solar Atlas's s Global Horizontal Irradiation distribution for Colombia
J | The capacity range is continuous across the different datasheets with a representative value selected through database processing and stakeholder consultation
K | The full-load hours are a result of global horizontal radiation, transposition factor and performance ratio.
L | Annual degradation of full load hours is not included in the above figures of full-load hours and capacity factors
References (from column K):
1 | UPME, “Incentivos tributarios para las FNCER” database, 2024
2 | Danish Energy Agency, Technology Catalogue for generation of electricity and District Heating, 2024
3 | Fraunhofer, 2024, Photovoltaics report 2024
4 | IEA, 2023, World Energy Outlook Global Energy and Climate Model input data
5 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
6 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
7 | Danish Energy Agency, Indian Technology Catalogue Generation and Storage of Electricity, 2022
8 | XM, Data from Paratec
9 | Emergente Energía Sostenible - Radiation Map for Colombia
10 | Discussion with Technology Catalogue stakeholder group
11 | World Bank, Global Solar Atlas

## 2.b. Industrial PV (rooftop)
| Technology | PV Industrial scale, rooftop - grid connected
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (kWe) | 100 | 100 | 100 | 20 | 1000 | 20 | 1000 | J | 7
| Forced outage (%) | 0 | 0 | 0 | [5 empty] | 2
| Planned outage (weeks per year) | 0 | 0 | 0 | [5 empty] | 2
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 30 | 40 |  | 2,5
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.5 | 1.5 |  | 5
| Space requirement (1000 m2/MWe) | 5.1 | 4.7674 | 4.1 | 4.4 | 6 | 3.5372 | 5.1765 |  | 5
Additional data for non thermal plants
| Capacity factor (%), theoretical | 18.7481 | 19.3162 | 20.4525 | 12.2944 | 27.5145 | 12.7442 | 30.498 | D,E | 5
| Capacity factor (%), incl. outages | 18.7481 | 19.3162 | 20.4525 | 12.2944 | 27.5145 | 12.7442 | 30.498 | D,E,F | 5
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | -
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | - | - | - | -
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| CH4 (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| N2O (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
Output
| Full load hours (kWh/kW) | 1642.3357 | 1692.1035 | 1791.639 | 1076.988 | 2410.2702 | 1116.39 | 2671.6248 | D,E,L
| Peak power full load hours (kWh/kWp) | 1368.6131 | 1410.0862 | 1493.0325 | 979.08 | 1854.054 | 1014.9 | 2055.096 | D,E,F,L
Financial data
| Specific investment, total system (M$/MWe) | 1.1802 | 0.81319 | 0.54542 | 1.1149 | 1.2874 | 0.51524 | 0.59495 | A,B,C | 1,2
| Specific investment, total system, per DC (M$/MWp) | 0.9835 | 0.67766 | 0.45451 | 1.0135 | 0.9903 | 0.4684 | 0.45765 | A,B,C | 1,2
| PV module cost ($/We(AC)) | 0.4636 | 0.30785 | 0.19805 | 0.43528 | 0.51041 | 0.18595 | 0.21804 | A,B,C | 1,2
| PV inverter cost ($/We(AC)) | 0.2022 | 0.13427 | 0.086378 | 0.18985 | 0.22262 | 0.081101 | 0.0951 | A,B,C | 1,2
| Balance Of Plant cost ($/We(AC)) | 0.2302 | 0.16606 | 0.1168 | 0.21891 | 0.24856 | 0.11107 | 0.12611 | A,B,C | 1
| Installation cost ($/We(AC)) | 0.2842 | 0.20501 | 0.1442 | 0.27026 | 0.30687 | 0.13712 | 0.1557 | A,B,C | 1,2
| Fixed O&M ($/MWe/year) | 15000 | 12900 | 10900 | 14600 | 15600 | 10600 | 11300 | C | 4,5,6,9
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1642.5 | 1642.5 | 1642.5 | 1194 | 2190 | 1194 | 2190 | I | 8,10
| DC/AC sizing factor (Wp/We) | 1.2 | 1.2 | 1.2 | 1.1 | 1.3 | 1.1 | 1.3 |  | 9
| Transposition Factor | 1.01 | 1.01 | 1.01 | 1 | 1.02 | 1 | 1.02 |  | 10
| Performance ratio | 0.825 | 0.85 | 0.9 | 0.82 | 0.83 | 0.85 | 0.92 | H | 2,3,9
| PV module conversion efficiency (%) | 21.5 | 23 | 25 |  |  |  |  | G | 2,3
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 2
| Average annual degradation of full-load hours (%) | 0.4 | 0.3 | 0.3 |  |  |  |  | K | 2
Financial data - per DC peak capacity
| Nominal investment (M$/MWp) | 0.9835 | 0.67766 | 0.45451 | 1.0135 | 0.9903 | 0.4684 | 0.45765 | A,B,C | 1,2
| PV module cost ($/Wp(DC)) | 0.38633 | 0.25654 | 0.16504 | 0.39571 | 0.39262 | 0.16904 | 0.16772 | A,B,C | 1,2
| PV inverter cost ($/Wp(DC)) | 0.1685 | 0.11189 | 0.071982 | 0.17259 | 0.17124 | 0.073728 | 0.073154 | A,B,C | 1,2
| Balance Of Plant cost ($/Wp(DC)) | 0.19183 | 0.13838 | 0.097331 | 0.19901 | 0.1912 | 0.10097 | 0.09701 | A,B,C | 1
| Installation cost ($/Wp(DC)) | 0.23683 | 0.17084 | 0.12016 | 0.24569 | 0.23605 | 0.12466 | 0.11977 | A,B,C | 1,2
| Fixed O&M ($/MWp(DC)/year) | 12500 | 10750 | 9083.3333 | 11230.7692 | 14181.8182 | 8153.8462 | 10272.7273 | C | 4,5,6,9
| Variable O&M ($/MWh_p(DC)) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Aggregated data of Colombian projects receiving incentives/support, in alignment with further international sources
B | Cost are projected with a learning rate approach assuming a 24 % learning rate for modules and inverters based on Fraunhofer, and 20 % as per other components based on IEA, and 10 % for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
C | Uncertainty in the short term assumes the same spread as the long-term uncertainty.
D | Capacity factor = Full load hours / 8760.
E | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1643 kWh/m2/year solar irradiation mentioned here, the capacity factors should be adjusted accordingly.
F | Yearly outage time is assumed to be 0,5 % equal approximately 2 hours.
G | The efficiency is a market average of commercial modules. Modules with above 21 % efficiency are commercially available. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon HJT n-type mono-Si cells which both have higher efficiencies.
H | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifier, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The IAM loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the MPPT efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules, which is assumed to be standard for ground-mounted plants in 2050.
I | The central value is the average annual solar irradiance received on a horizontal surface in Colombia. The areas receiving the highest levels of global solar radiation, exceeding the San Andrés and Providencia islands, large parts of the Caribbean region, and the inter-Andean valley. Minimum and maximum value correspond to The Global Solar Atlas's s Global Horizontal Irradiation distribution for Colombia
J | The capacity range is continuous across the different datasheets with a representative value selected through database processing and stakeholder consultation
K | Annual degradation of full load hours is not included in the above figures of full-load hours and capacity factors
L | The full-load hours are a result of global horizontal radiation, transposition factor and performance ratio.
References (from column K):
1 | UPME, “Incentivos tributarios para las FNCER” database, 2024
2 | Danish Energy Agency, Technology Catalogue for generation of electricity and District Heating, 2024
3 | Fraunhofer, 2024, Photovoltaics report 2024
4 | IEA, 2023, World Energy Outlook Global Energy and Climate Model input data
5 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
6 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
7 | XM, Data from Paratec
8 | Emergente Energía Sostenible - Radiation Map for Colombia
9 | Discussion with Technology Catalogue stakeholder group
10 | World Bank, Global Solar Atlas

## 2.c. Small scale PV
| Technology | PV small scale, ground-mounted - grid connected
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for a typical power plant (MWe) | 10 | 10 | 10 | 1 | 20 | 1 | 20 | L | 5
| Forced outage (%) | 0 | 0 | 0 | [5 empty] | 2
| Planned outage (weeks per year) | 1 | 1 | 1
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 30 | 40 |  | 2,7
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.5 | 1.5 |  | 7
| Space requirement (1000 m2/MWp) | 12.5 | 11.6848 | 10.0489 | 6 | 13 | 6 | 13 | M | 8
Additional data for non thermal plants
| Capacity factor (%), theoretical | 20.3105 | 20.9259 | 22.6492 | 12.2944 | 33.864 | 12.7442 | 37.536 | F,G | 7
| Capacity factor (%), incl. outages | 19.9199 | 20.5235 | 22.2137 | 12.2944 | 33.864 | 12.7442 | 37.536 | F,G,H | 7
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | -
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | - | - | - | -
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| CH4 (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| N2O (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
Output
| Full load hours (kWh/kW) | 1779.1971 | 1833.1121 | 1984.0743 | 1076.988 | 2966.4864 | 1116.39 | 3288.1536 | F,G,O
| Peak power full load hours (kWh/kWp) | 1368.6131 | 1410.0862 | 1526.211 | 979.08 | 1854.054 | 1014.9 | 2055.096 | F,G,H,O
Financial data
| Specific investment, total system (M$/MWe) | 1.1189 | 0.77252 | 0.51928 | 1.0573 | 1.2199 | 0.4907 | 0.56617 | A,B,C | 1,2,10
| Specific investment, total system, per DC (M$/MWp) | 0.86069 | 0.59425 | 0.39944 | 0.96121 | 0.76246 | 0.44609 | 0.35385 | A,B,C,D | 1,2
| PV module cost ($/We(AC)) | 0.4639 | 0.30805 | 0.19817 | 0.43556 | 0.51074 | 0.18607 | 0.21818 | A,B,C | 1,2
| PV inverter cost ($/We(AC)) | 0.14 | 0.092966 | 0.059807 | 0.13145 | 0.15414 | 0.056153 | 0.065845 | A,B,C | 1,2
| Balance Of Plant cost ($/We(AC)) | 0.285 | 0.20559 | 0.1446 | 0.27102 | 0.30773 | 0.13751 | 0.15613 | A,B,C | 1
| Installation cost ($/We(AC)) | 0.23 | 0.16591 | 0.1167 | 0.21872 | 0.24834 | 0.11097 | 0.126 | A,B,C | 1,2
| Fixed O&M ($/MWe/year) | 11000 | 9400 | 8000 | 10700 | 11400 | 7800 | 8300 | C,E | 6
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1642.5 | 1642.5 | 1642.5 | 1194 | 2190 | 1194 | 2190 | K | 4,9
| DC/AC sizing factor (Wp/W) | 1.3 | 1.3 | 1.3 | 1.1 | 1.6 | 1.1 | 1.6 | D | 10
| Transposition Factor | 1.01 | 1.01 | 1.01 | 1 | 1.02 | 1 | 1.02 |  | 9
| Performance ratio [-] | 0.825 | 0.85 | 0.92 | 0.82 | 0.83 | 0.85 | 0.92 | J | 2,3,8
| PV module conversion efficiency (%) | 21.5 | 23 | 25 |  |  |  |  | I | 2,3
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 2
| Average annual degradation of full-load hours (%) | 0.4 | 0.3 | 0.3 |  |  |  |  | N | 2
Financial data - per DC peak capacity
| Nominal investment (M$/MWp) | 0.86069 | 0.59425 | 0.39944 | 0.96121 | 0.76246 | 0.44609 | 0.35385 | A,B,C,D | 1,2
| PV module cost ($/Wp(DC)) | 0.35685 | 0.23696 | 0.15244 | 0.39596 | 0.31921 | 0.16915 | 0.13636 | A,B,C | 1,2
| PV inverter cost ($/Wp(DC)) | 0.10769 | 0.071512 | 0.046005 | 0.1195 | 0.096335 | 0.051048 | 0.041153 | A,B,C | 1,2
| Balance Of Plant cost ($/Wp(DC)) | 0.21923 | 0.15815 | 0.11123 | 0.24638 | 0.19233 | 0.12501 | 0.097584 | A,B,C | 1
| Installation cost ($/Wp(DC)) | 0.17692 | 0.12763 | 0.089766 | 0.19884 | 0.15522 | 0.10088 | 0.078752 | A,B,C | 1,2
| Fixed O&M ($/MWp(DC)/year) | 8461.5385 | 7230.7692 | 6153.8462 | 6687.5 | 10363.6364 | 4875 | 7545.4545 | C,E | 6
| Variable O&M ($/MWh_p(DC)) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Aggregated data of Colombian projects receiving incentives/support, supplemented with further international sources
B | Cost are projected with a learning rate approach assuming a 24 % learning rate for modules and inverters based on Fraunhofer, and 20 % as per other components based on IEA, and 10 % for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
C | Uncertainty in the short term assumes the same spread as the long-term uncertainty
D | The typical sizing factor is based on operational projects, expressed in their average for the central value and minimum and maximum for the lower and higher bound. Most projects are designed around the central value for both small-scale and large-scale plants.
E | IRENA data representative for utility-scale plants converted to smaller scale plants
F | Capacity factor = Full load hours / 8760.
G | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1643 kWh/m2/year solar irradiation mentioned here, the capacity factors should be adjusted accordingly.
H | Yearly outage time is assumed to be 0,5 % equal approximately 2 hours.
I | The efficiency is a market average of commercial modules. Modules with above 21% efficiency are commercially available. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon HJT n-type mono-Si cells which both have higher efficiencies.
J | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifier, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The IAM loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the MPPT efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules, which is assumed to be standard for ground-mounted plants in 2050.
K | The central value is the average annual solar irradiance received on a horizontal surface in Colombia. The areas receiving the highest levels of global solar radiation, exceeding the San Andrés and Providencia islands, large parts of the Caribbean region, and the inter-Andean valley. Minimum and maximum value correspond to The Global Solar Atlas's s Global Horizontal Irradiation distribution for Colombia
L | The capacity range is continuous across the different datasheets with a representative value selected through database processing and stakeholder consultation
M | Typical size identified through stakeholder consultation, and projected as per assumed efficiency gain of modules. Typically, tracking projects use 20 % more land compared to fixed-tilt projects based on stakeholder consultation.
N | Annual degradation of full load hours is not included in the above figures of full-load hours and capacity factors
O | The full-load hours are a result of global horizontal radiation, transposition factor and performance ratio.
References (from column K):
1 | UPME, “Incentivos tributarios para las FNCER” database, 2024
2 | Danish Energy Agency, Technology Catalogue for generation of electricity and District Heating, 2024
3 | Fraunhofer, 2024, Photovoltaics report 2024
4 | Emergente Energía Sostenible - Radiation Map for Colombia
5 | XM, Data from Paratec
6 | IRENA, 2023, Renewable Power Generation Costs in 2022
7 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
8 | Discussion with Technology Catalogue stakeholder group
9 | World Bank, Global Solar Atlas
10 | Bloomberg New Energy Finance, Power Asset Database

## 2.d. Utility scale PV(tracking)
| Technology | PV utility-scale, ground-mounted - grid connected
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity a typical power plant (MWe) | 70 | 70 | 70 | 20 | 150 | 20 | 150 | J | 6
| Forced outage (%) | 0 | 0 | 0 | [5 empty] | 2
| Planned outage (weeks per year) | 1 | 1 | 1
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 30 | 40 |  | 2,7
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.5 | 1.5 |  | 7
| Space requirement (1000 m2/MWp) | 15 | 14.5588 | 13.0555 | 7.2 | 15.6 | 7.2 | 15.6 | K | 8
Additional data for non-thermal plants
| Capacity factor (%), theoretical | 25.3881 | 26.1574 | 28.3116 | 17.4636 | 39.6844 | 18.1025 | 43.9875 | F | 7
| Capacity factor (%), incl. outages | 24.8999 | 25.6544 | 27.7671 | 17.4636 | 39.6844 | 18.1025 | 43.9875 | F | 7
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | -
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | - | - | - | -
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| CH4 (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| N2O (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
Output
| Full load hours (kWh/kW) | 2223.9963 | 2291.3902 | 2480.0929 | 1529.8125 | 3476.3513 | 1585.7812 | 3853.305 | F,M
| Peak power full load hours (kWh/kWp) | 1710.7664 | 1762.6078 | 1907.7638 | 1223.85 | 2317.5675 | 1268.625 | 2568.87 | F,M
Financial data
| Specific investment, total system (M$/MWe) | 1.0329 | 0.71287 | 0.47898 | 0.976 | 1.1263 | 0.45259 | 0.52228 | A,B,C | 1,2
| Specific investment, total system, per DC (M$/MWp) | 0.79454 | 0.54836 | 0.36845 | 0.7808 | 0.75085 | 0.36207 | 0.34818 | A,B,C,E | 1,2
| PV module cost ($/We(AC)) | 0.4245 | 0.28189 | 0.18134 | 0.39857 | 0.46736 | 0.17026 | 0.19965 | A,B,C | 1,2
| PV inverter cost ($/We(AC)) | 0.1378 | 0.091505 | 0.058867 | 0.12938 | 0.15171 | 0.055271 | 0.064811 | A,B,C | 1,2
| Nominal investment (tracker related costs) ($/We(AC)) | 0.05 | 0.036068 | 0.025369 | 0.047548 | 0.053988 | 0.024124 | 0.027392 | A,B,C,D | 1,2
| Balance Of Plant cost ($/We(AC)) | 0.23 | 0.16591 | 0.1167 | 0.21872 | 0.24834 | 0.11097 | 0.126 | A,B,C | 1
| Installation cost ($/Wp) | 0.1906 | 0.13749 | 0.096705 | 0.18125 | 0.2058 | 0.091962 | 0.10442 | A,B,C | 1,2
| Fixed O&M ($/MWe/year) | 7400 | 6300 | 5400 | 7100 | 7700 | 5200 | 5600 | B,C | 5
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1642.5 | 1642.5 | 1642.5 | 1194 | 2190 | 1194 | 2190 | I | 4,9
| DC/AC sizing factor (Wp/W) | 1.3 | 1.3 | 1.3 | 1.25 | 1.5 | 1.25 | 1.5 | E | 10
| Transposition Factor | 1.2625 | 1.2625 | 1.2625 | 1.25 | 1.275 | 1.25 | 1.275 |  | 9
| Performance ratio [-] | 0.825 | 0.85 | 0.92 | 0.82 | 0.83 | 0.85 | 0.92 | H | 2,3,8
| PV module conversion efficiency (%) | 21.5 | 23 | 25 |  |  |  |  | G | 2,3
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 2
| Average annual degradation of full-load hours (%) | 0.4 | 0.3 | 0.3 |  |  |  |  | L | 2
Financial data
| Nominal investment (M$/MWp) | 0.79454 | 0.28189 | 0.18134 | 0.39857 | 0.46736 | 0.17026 | 0.19965 | A,B,C,E | 1,2
| PV module cost ($/Wp(DC)) | 0.32654 | 0.21684 | 0.13949 | 0.31885 | 0.31157 | 0.13621 | 0.1331 | A,B,C | 1,2
| PV inverter cost ($/Wp(DC)) | 0.106 | 0.070389 | 0.045282 | 0.10351 | 0.10114 | 0.044217 | 0.043207 | A,B,C | 1,2
| Nominal investment (tracker related costs) ($/Wp(DC)) | 0.038462 | 0.027745 | 0.019514 | 0.038038 | 0.035992 | 0.0193 | 0.018261 | A,B,C,D | 1,2
| Installation cost ($/Wp(DC)) | 0.17692 | 0.12763 | 0.089766 | 0.17498 | 0.16556 | 0.088778 | 0.084002 | A,B,C | 1
| Balance Of Plant cost ($/Wp(DC)) | 0.14662 | 0.10576 | 0.074389 | 0.145 | 0.1372 | 0.07357 | 0.069612 | A,B,C | 1,2
| Fixed O&M ($/MWp(DC)/year) | 5692.3077 | 4846.1538 | 4153.8462 | 4733.3333 | 6160 | 3466.6667 | 4480 | B,C | 5
| Variable O&M ($/MWh_p(DC)) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Aggregated data of Colombian projects receiving incentives/support, supplemented with further international sources
B | Cost are projected with a learning rate approach assuming a 24 % learning rate for modules and inverters based on Fraunhofer, and 20 % as per other components based on IEA, and 10 % for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
C | Uncertainty in the short term assumes the same spread as the long-term uncertainty
D | Tracker-related cost usually amounts to 10 – 15 % of the cost, including its installation
E | The typical sizing factor is based on operational projects, expressed in their average for the central value and minimum and maximum for the lower and higher bound. Most projects are designed around the central value for both small-scale and large-scale plants.
F | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1643 kWh/m2/year solar irradiation mentioned here, the capacity factors should be adjusted accordingly.
G | The efficiency is a market average of commercial modules. Modules with above 21% efficiency are commercially available. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon HJ) n-type mono-Si cells which both have higher efficiencies.
H | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifier, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The IAM loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the MPPT efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules, which is assumed to be standard for ground-mounted plants in 2050.
I | The central value is the average annual solar irradiance received on a horizontal surface in Colombia. The areas receiving the highest levels of global solar radiation, exceeding the San Andrés and Providencia islands, large parts of the Caribbean region, and the inter-Andean valley. Minimum and maximum value correspond to The Global Solar Atlas's s Global Horizontal Irradiation distribution for Colombia
J | The capacity range is continuous across the different datasheets with a representative value selected through database processing and stakeholder consultation. The upper range corresponds to the largest PV plant in operation in Colombia as of September 2024.
K | Typical size identified through stakeholder consultation, and projected as per assumed efficiency gain of modules. Typically, tracking projects use 20% more land compared to fixed-tilt projects based on stakeholder consultation.
L | Annual degradation of full load hours is not included in the above figures of full-load hours and capacity factors
M | The full-load hours are a result of global horizontal radiation, transposition factor and performance ratio.
References (from column K):
1 | UPME, “Incentivos tributarios para las FNCER” database, 2024
2 | Danish Energy Agency, Technology Catalogue for generation of electricity and District Heating, 2024
3 | Fraunhofer, 2024, Photovoltaics report 2024
4 | Emergente Energía Sostenible - Radiation Map for Colombia
5 | IRENA, 2023, Renewable Power Generation Costs in 2022
6 | XM, Data from Paratec
7 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
8 | Discussion with Technology Catalogue stakeholder group
9 | World Bank, Global Solar Atlas
10 | Bloomberg New Energy Finance, Power Asset Database

## 2.e. Floating PV
| Technology | PV Floating, utility-scale, grid connected
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (MWe) | 10 | 10 | 10 | 1 | 20 | 1 | 20 | H
| Forced outage (%) | 0 | 0 | 0 | [5 empty] | 2,6
| Planned outage (weeks per year) | 1 | 1 | 1 | [5 empty] | 2,6
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 30 | 40 |  | 2,6
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.5 | 1.5 |  | 2,6
| Space requirement (1000 m2/MWe) | 12.5 | 11.6848 | 10.0489 | 6 | 13 | 6 | 13 |  | 2,6
Additional data for non thermal plants
| Capacity factor (%), theoretical | 21.2952 | 21.4183 | 22.6492 | 13.9709 | 33.3349 | 14.482 | 35.19 | K | 2
| Capacity factor (%), incl. outages | 20.8857 | 21.0064 | 22.2137 | 13.9709 | 33.3349 | 14.482 | 35.19 | K | 2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | -
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | - | - | - | -
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| CH4 (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
| N2O (g per GJ fuel) | 0 | 0 | 0 | - | - | - | -
Output
| Full load hours (kWh/kW) | 1865.4612 | 1876.2442 | 1984.0743 | 1223.85 | 2920.1351 | 1268.625 | 3082.644 | K
| Peak power full load hours (kWh/kWp) | 1434.9701 | 1443.2648 | 1526.211 | 979.08 | 1946.7567 | 1014.9 | 2055.096 | K
Financial data
| Specific investment, total system (M$/MWe) | 1.3764 | 0.95827 | 0.64993 | 1.3023 | 1.4978 | 0.61494 | 0.70723 | A,B,C | 1,2
| Specific investment, total system, per DC (M$/MWp) | 1.0588 | 0.73713 | 0.49994 | 1.0418 | 0.99851 | 0.49195 | 0.47149 | A,B,C,D | 1,2
| PV module cost ($/We(AC)) | 0.4639 | 0.30805 | 0.19817 | 0.43556 | 0.51074 | 0.18607 | 0.21818 | A,B,C | 1,2
| PV inverter cost ($/We(AC)) | 0.14 | 0.092966 | 0.059807 | 0.13145 | 0.15414 | 0.056153 | 0.065845 | A,B,C | 1,2
| Balance Of Plant cost ($/We(AC)) | 0.4275 | 0.30838 | 0.2169 | 0.40653 | 0.4616 | 0.20626 | 0.2342 | A,B,C | 1,2
| Installation cost ($/We(AC)) | 0.345 | 0.24887 | 0.17504 | 0.32808 | 0.37252 | 0.16646 | 0.189 | A,B,C | 1,2
| Fixed O&M ($/MWe/year) | 13750 | 11800 | 10000 | 13300 | 14200 | 9700 | 10300 | A,C | 1,2
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1642.5 | 1642.5 | 1642.5 | 1194 | 2190 | 1194 | 2190 | G | 4,7
| DC/AC sizing factor (Wp/W) | 1.3 | 1.3 | 1.3 | 1.25 | 1.5 | 1.25 | 1.5 | D | 8
| Transposition Factor | 1.01 | 1.01 | 1.01 | 1 | 1.02 | 1 | 1.02 |  | 7
| Performance ratio | 0.865 | 0.87 | 0.92 | 0.82 | 0.8715 | 0.85 | 0.92 | F,I | 2,3,5
| PV module conversion efficiency (%) | 21.5 | 23 | 25 |  |  |  |  | E | 2,3
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 2
| Average annual degradation of full-load hours (%) | 0.4 | 0.3 | 0.3 |  |  |  |  | J | 6
Financial data - per DC peak capacity
| Nominal investment (M$/MWp) | 1.0588 | 0.73713 | 0.49994 | 1.0418 | 0.99851 | 0.49195 | 0.47149 | A,B,C,D | 1,2
| PV module cost ($/Wp(DC)) | 0.35685 | 0.23696 | 0.15244 | 0.34845 | 0.34049 | 0.14885 | 0.14546 | A,B,C | 1,2
| PV inverter cost ($/Wp(DC)) | 0.10769 | 0.071512 | 0.046005 | 0.10516 | 0.10276 | 0.044922 | 0.043897 | A,B,C | 1,2
| Balance Of Plant cost ($/Wp(DC)) | 0.32885 | 0.23722 | 0.16685 | 0.32523 | 0.30773 | 0.16501 | 0.15613 | A,B,C | 1,2
| Installation cost ($/Wp(DC)) | 0.26538 | 0.19144 | 0.13465 | 0.26246 | 0.24834 | 0.13317 | 0.126 | A,B,C | 1,2
| Fixed O&M ($/MWp(DC)/year) | 10576.9231 | 9076.9231 | 7692.3077 | 8866.6667 | 11360 | 6466.6667 | 8240 | A,C | 1,2
| Variable O&M ($/MWh_p(DC)) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Overall cost estimation based on utility-scale datasheet, considering that floating PV plants are expected ca. 25 % more expensive than ground-mounted utility-scale plants, with the mark-up apparent in installation and other cost incl. balance of plant
B | Cost are projected with a learning rate approach assuming a 24 % learning rate for modules and inverters based on Fraunhofer, and 20% as per other components based on IEA, and 10 % for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
C | Uncertainty in the short term assumes the same spread as the long-term uncertainty
D | The typical sizing factor is based on operational projects (both floating and ground-mounted plants), expressed in their average for the central value and minimum and maximum for the lower and higher bound.
E | The efficiency is a market average of commercial modules. Modules with above 21 % efficiency are commercially available. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon HJT n-type mono-Si cells which both have higher efficiencies.
F | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifier, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The IAM loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the MPPT efficiency and is averaged over typical load levels.
G | The central value is the average annual solar irradiance received on a horizontal surface in Colombia. The areas receiving the highest levels of global solar radiation, exceeding the San Andrés and Providencia islands, large parts of the Caribbean region, and the inter-Andean valley. Minimum and maximum value correspond to The Global Solar Atlas's s Global Horizontal Irradiation distribution for Colombia
H | The capacity range equals the size for small-scale ground-mounted PV plants for easier comparison between the datasheets. As of 2024, there are no floating PV plants of that size commissioned in Colombia and global experience on this scale is sparse.
I | The surrounding water can have an effect on the performance ratio in terms of its cooling and reflective properties, which typically lies 5% above comparable ground-mounted onshore PV plants.
J | Annual degradation of full load hours is not included in the above figures of full-load hours and capacity factors
K | The full-load hours are a result of global horizontal radiation, transposition factor and performance ratio.
References (from column K):
1 | UPME, “Incentivos tributarios para las FNCER” database, 2024
2 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
3 | Fraunhofer, 2024, Photovoltaics report 2024
4 | Emergente Energía Sostenible - Radiation Map for Colombia
5 | Discussion with Technology Catalogue stakeholder group
6 | Danish Energy Agency, Technology Catalogue for generation of electricity and District Heating, 2024
7 | World Bank, Global Solar Atlas
8 | Bloomberg New Energy Finance, Power Asset Database

## 3.a. Wind Onshore
| Technology | Wind power - Onshore
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 4.5 | 6.2 | 7 | 2 | 5.6 | 5.5 | 9 |  | 2,3,9
| Generating capacity for total power plant (MWe) | 100 | 100 | 100 | 10 | 300 | 10 | 300 |  | 9,11
| Forced outage (%) | 2.5 | 2 | 2 | [5 empty] | 3
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | [5 empty] | 3
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 2,3
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 2
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | [5 empty] | 3
| Average annual full-load hours (MWhe/MWe) | 3066 | 3300 | 3700 | [5 empty] | 10
Additional data for non thermal plants
| Capacity factor (%), theoretical | 36.6876 | 39.2862 | 44.0482 |  |  |  |  | E
| Capacity factor (%), incl. outages | 35 | 37.6712 | 42.2374 | 24 | 46 | 24 | 46 | E | 8
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | -
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Specific investment, total system (M$/MW) | 1.37 | 1.3002 | 1.2312 | 1.1 | 1.5 | 1.2023 | 1.2646 | A,D | 1,2,3,4,5,6,9
| - of which equipment | 0.959 | 0.91012 | 0.86184 | 0.77 | 1.05 | 0.84163 | 0.88524 | B,D | 2,3,4,9
| - of which installation | 0.411 | 0.39005 | 0.36936 | 0.33 | 0.45 | 0.3607 | 0.37939 | B,D | 2,3,4,9
| Fixed O&M ($/MWe/year) | 27400 | 26000 | 24600 | 22000 | 30000 | 24000 | 25500 | C,D | 1,2,3,4,5,6,9
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
| Hub Height (m) | 85 | 130 | 150 | 85 | 120 | 85 | 150 |  | 2,3,9
| Rotor Diameter (m) | 135 | 162 | 190 | [5 empty] | 9
| Specific Power (W/m2) | 314.3801 | 300.7958 | 246.8886 | [5 empty] | 2,3,9
Notes (from column J):
A | Given the early stage onshore wind market in Colombia, the values are an aggregated assessment on literature supplemented by data aggregation of data of the register of UPME
B | Equipment: Cost of turbines including transportation. Installation: Electrical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project. Central value assumes a 70/30 distribution.
C | O&M corresponding to 2 % of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors all O&M is accrued under fixed for simplicity
D | Cost are projected with a learning rate approach assuming a 5% learning rate based on [1] and [2], and 6 % learning rate for OPEX based on [2]. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
E | This data is from Jepirachi, the only project in Colombia that went in commercial operation
F | The average project size is done in discussion with stakeholders, and is aligned with the average size of Colombian projects for which financing is secured. The uncertainty range shows the wide spread of these projects.
References (from column K):
1 | UPME, “Registro de Proyectos de Generación” database
2 | Danish Energy Agency, Technology Catalogue for generation of electricity and District Heating, 2024
3 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
4 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
5 | Danish Energy Agency, Indian Technology Catalogue Generation and Storage of Electricity, 2022
6 | IEA, 2023, World Energy Outlook Global Energy and Climate Model input data
7 | IRENA, 2023, Renewable Power Generation Costs in 2022
8 | Calculation from Sinergox - Data Provided by MME
9 | Discussion with Technology Catalogue stakeholder group
10 | World Bank, Global Wind Atlas
11 | Bloomberg New Energy Finance, Power Asset Database

## 3.b. Small wind onshore
| Technology | Wind power - Small onshore wind turbines < 1 MW
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 0.01 | 0.01 | 0.01 | 0.005 | 0.025 | 0.005 | 0.025 |  | 1,2
| Generating capacity for total power plant (MWe) | 1 | 5 | 10 | 1 | 10 | 1 | 10 |  | 3
| Forced outage (%) | 2 | 1.5 | 1.5 | 0 | 8 | 0 | 8 |  | 1,2,3
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | [5 empty] | 1,2,3
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 1,2
| Construction time (years) | 1 | 1 | 1 | [5 empty] | 1,2,3
| Space requirement (1000 m2/MWe) | 11 | 11 | 11 | [5 empty] | 2,3
Additional data for non thermal plants
| Capacity factor (%), theoretical | 26.0717 | 25.9394 | 25.9394 | 20 | 32.6087 | 20 | 32.6087 |  | 3
| Capacity factor (%), incl. outages | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | -
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Specific investment, total system (M$/MW) | 3.4253 | 3.2507 | 3.0783 | 2.9855 | 3.8006 | 3.0061 | 3.1619 | A,D | 1
| - of which equipment | 2.3977 | 2.2755 | 2.1548 | 2.0898 | 2.6604 | 2.1043 | 2.2133 | B,D | 1
| - of which installation | 1.0276 | 0.97522 | 0.92349 | 0.89564 | 1.1402 | 0.90183 | 0.94856 | B,D | 1
| Fixed O&M ($/MWe/year) | 68500 | 64300 | 60200 | 51375 | 85625 | 45150 | 75250 | C,D | 1,2
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Values are in line with [1] and [2], expressing the small-scale wind turbines with a 0.8 proportionality factor compared to the large-scale turbines. The cost varies significantly based on different designs and types of small-scale wind
B | Uncertainty of investment cost for the base year is assumed to scale with the proportionality factor depending on capacity sizes, with lower cost due to higher capacity rating employed
C | The fixed O&M corresponds to 2.7 % of CAPEX/year given the same proportionality factor between large-scale and small-scale wind. Uncertainty values assumed to be +/-25 %
D | Cost are projected with a learning rate approach assuming a 5% learning rate based on [1] and [2], and 6% learning rate for OPEX based on [2]. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
E | A proportionality factor α of 0.85 is used to convert the presented cost from the utility-scale datasheet to small-scale, in accordance with economy of scale found in literature and in line with input given by stakeholders
F | Uncertainty for O&M is based on a +/- 25 % spread in line with [2]
References (from column K):
1 | Danish Energy Agency, Technology Catalogue for generation of electricity and District Heating, 2024
2 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
3 | Discussion with Technolgy Catalogue stakeholder group

## 4.a. Wind Offshore fixed bottom
| Technology | Wind power - Offshore
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 8 | 15 | 20 | [5 empty] | 1,3,4
| Generating capacity for total power plant (MWe) | 200 | 500 | 1000 | [5 empty] | 1,3,4,10
| Hub Height (m) | 100 | 135 | 155 | [5 empty] | 1
| Forced outage (%) | 0.04 | 0.03 | 0.02 | [5 empty] | 1,3,4
| Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1,3,4
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 30 | 25 | 35 |  | 1
| Construction time (years) | 3 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 1,3,4
| Space requirement (1000 m2/MWe) | 137.7075 | 178.2272 | 167.96 |  |  |  |  | G
| Average annual full-load hours (MWhe/MWe) | 3500 | 4800 | 4900 | [5 empty] | 1,3,9,10
Additional data for non thermal plants
| Capacity factor (%), theoretical | 42 | 57.0776 | 57.6484 | 35 | 45 | 35 | 60 | F | 1,3,9,10
| Capacity factor (%), incl. outages | 39.9323 | 54.8329 | 55.9522 |  |  |  |  | F
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | E | 1,3,4
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Specific investment, total system (M$/MW) | 4.3378 | 3.2383 | 2.2686 | 4 | 5 | 2.2384 | 2.6077 | A,D | 2,3,6,8
| - of which equipment | 2.1689 | 1.6191 | 1.1343 | 2 | 2.5 | 1.1192 | 1.3038 | B,D | 6
| - of which installation | 1.3014 | 0.97149 | 0.68057 | 1.2 | 1.5 | 0.67152 | 0.7823 | B,D | 6
| - of which grid connection | 0.86757 | 0.64766 | 0.45371 | 0.8 | 1 | 0.44768 | 0.52153 | B,D | 6
| Fixed O&M ($/MWe/year) | 108500 | 81000 | 56500 | 100000 | 125000 | 56000 | 65000 | C,D | 2,3,6,7
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Rotor diameter (m) | 164 | 236 | 270 | [5 empty] | 1
| Hub height (m) | 100 | 135 | 155 | [5 empty] | 1
| Specific power (W/m2) | 378.7149 | 342.9078 | 349.3113 | [5 empty] | 1
| Availability (%) | 95.0769 | 96.0673 | 97.0577 | [5 empty] | 1,3,9
Notes (from column J):
A | Given the nascent offshore wind market in Colombia, the values are an aggregated assessment on literature supplemented by data aggregation of data of the register of UPME. There is large uncertainty on these values
B | Cost breakdown can vary significantly based on site characteristics. Here 50 %, 30 %, and 20 % for equipment, installation and grid connection are assumed for modelling purposes only, consulting global IRENA data
C | O&M corresponding to 2.5 % of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors, all O&M is for simplicity accrued under fixed O&M
D | Cost are projected with a learning rate approach assuming a 15 % learning rate based on IEA, and 8 % learning rate for OPEX. There is high uncertainty given the nascent market stage, which could result in higher learnings after the first of a kind project. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
E | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
F | Capacity factors are highly dependent on the wind climate. For 2024, wind speeds of 8-9 m/s are chosen representing the favourable conditions for fixed bottom offshore wind off the coast between Cartagena and Barranquilla. From 2030 onwards, the wind climate conditions around La Guajira are chosen, assuming the availability for offtake following the commissioning of HVDC line to the region as per UPME's transmission expansion plans.
G | Calculated based on average spacing of 8 RD between turbines and a square layout. Space requirement is highly depending on site size, layout and chosen distance between turbines.
References (from column K):
1 | Danish Energy Agency, Technology Catalogue for generation of electricity and District Heating, 2024
2 | UPME, “Registro de Proyectos de Generación” database
3 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
4 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
5 | Danish Energy Agency, Indian Technology Catalogue Generation and Storage of Electricity, 2022
6 | IEA, 2023, World Energy Outlook Global Energy and Climate Model input data
7 | IRENA, 2023, Renewable Power Generation Costs in 2022
8 | Discussion with Technology Catalogue stakeholder group
9 | World Bank, Global Wind Atlas
10 | AFRY, Offshore Wind Roadmap Study, Hoja de ruta para el despliegue de la energía eólica costa afuera en Colombia, 2024

## 4.b. Wind offshore floating
| Technology | Wind power - Floating offshore
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | - | 15 | 20 | - | - |  |  |  | 1,2,3
| Generating capacity for total wind farm (MWe) | - | 150 | 1000 | - | - |  |  |  | 1,2,3,6
| Forced outage (%) | - | 0.03 | 0.02 | - | - |  |  |  | 1,2,3
| Planned outage (weeks per year) | - | 0.5 | 0.5 | - | - |  |  |  | 1,2,3
| Technical lifetime (years) | - | 30 | 30 | - | - |  |  |  | 1,2,3
| Construction time (years) | - | 2.5 | 2.5 | - | - |  |  |  | 1,2,3
| Space requirement (1000 m2/MWe) | - | 95.05 | 167.96 | - | - |  |  | C
| Average annual full-load hours [MWh_e/MW_e] | - | 4800 | 4900 | - | - |  |  |  | 1,3,5
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | 57.0776 | 57.6484 | - | - | 45 | 60 | D | 1,3,5,6
| Capacity factor (%), incl. outages | - | 54.8329 | 55.9522 | - | - |  |  | D
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | -
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | - | 0 | 0 | - | - | 0 | 0
| SO2 (degree of desulphuring, %) | - | 0 | 0 | - | - | 0 | 0
| NOX (g per GJ fuel) | - | 0 | 0 | - | - | 0 | 0
| CH4 (g per GJ fuel) | - | 0 | 0 | - | - | 0 | 0
| N2O (g per GJ fuel) | - | 0 | 0 | - | - | 0 | 0
Financial data
| Specific investment, total system (M$/MW) | - | 5.4223 | 2.8357 | - | - | 2.798 | 3.2596 | B | 2,3,4
| - of which equipment | - | 2.7111 | 1.4179 | - | - | 1.399 | 1.6298 | B | 2,3,4
| - of which installation | - | 1.6267 | 0.85071 | - | - | 0.83939 | 0.97787 | B | 2,3,4
| - of which grid connection | - | 1.0845 | 0.56714 | - | - | 0.5596 | 0.65192 | B | 2,3,4
| Fixed O&M ($/MWe/year) | - | 135625 | 70625 | - | - | 70000 | 81250 | B,E | 2,3,4
| Variable O&M ($/MWh) | - | 0 | 0 | - | - | 0 | 0
| Start-up costs ($/MWe/start-up) | - | 0 | 0 | - | - | 0 | 0
Technology specific data
| Rotor diameter (m) | - | 236 | 270 | - | - |  |  |  | 1
| Hub height (m) | - | 135 | 155 | - | - |  |  |  | 1
| Specific power (W/m2) | - | 342.9078 | 349.3113 | - | - |  |  |  | 1
| Availability (%) | - | 96.0673 | 97.0577 | - | - |  |  |  | 1,3,9
Notes (from column J):
A | Floating offshore is not assumed earlier than 2030, with commercialisation planned for 2035 as mentioned in [6]
B | For the initial cost CAPEX and OPEX assessments, it is assumed that Floating offshore is 25% more expensive than fixed bottom offshore. For the initial year 2030, the comparison is against 2024 fixed bottom costs. Results are in line with [2] and [3]
C | Calculated based on average spacing of 8 RD between turbines and a square layout. Space requirement is highly depending on site size, layout and chosen distance between turbines.
D | Capacity factors are highly dependent on the wind climate. Assumptions for the central value are based on the wind climate off the coast of La Guajira.
E | O&M corresponding to 2.5% of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors, all O&M is for simplicity accrued under fixed O&M
References (from column K):
1 | Danish Energy Agency, Technology Catalogue for Generation of Electricity and District Heating, 2024
2 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
3 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
4 | IEA, 2023, World Energy Outlook Global Energy and Climate Model input data
5 | World Bank, Global Wind Atlas
6 | AFRY, Offshore Wind Roadmap Study, Hoja de ruta para el despliegue de la energía eólica costa afuera en Colombia, 2024

## 5.a. Large RoR hydro power
| Technology | Hydro power plant - large system
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 35 | 35 | 35 | 20 | 50 | 20 | 50 | A | 1,6,11
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 |  | 8
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 |  | 8
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 9
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 9
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 8
| Construction time (years) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 3,11
| Space requirement (1000 m2/MWe) | 2,4 | 2,4 | 2,4 | 1,4 | 3,2 | 1,4 | 3,2 | G | 10,11
Additional data for non thermal plants
| Capacity factor (%), theoretical | 53.0612 | 53.0612 | 53.0612 | 37.6812 | 65.7959 | 37.6812 | 65.7959 | H
| Capacity factor (%), incl. outages | 48 | 48 | 48 | 31 | 62 | 31 | 62 | H | 6,7
Ramping configurations
| Ramping (% per minute) | 55 | 55 | 55 | 0 | 100 | 0 | 100 | H | 6,12
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12
| Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0 | 0.5 | 0 | 0.5 |  | 6
| Cold start-up time (hours) | 0.3 | 0.3 | 0.3 | 0 | 0.5 | 0 | 0.5 |  | 6
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2.5 | 2.4955 | 2.4828 | 2.2 | 3 | 2.1849 | 2.9794 | B,E,I | 2,3,4,5,11
| - of which equipment | 0.9 | 0.89839 | 0.89382 | 0.792 | 1.08 | 0.78656 | 1.0726 | C,E,I | 2,3,4,11
| - of which installation | 1.6 | 1.5971 | 1.589 | 1.408 | 1.92 | 1.3983 | 1.9068 | C,E,I | 2,3,4,11
| Fixed O&M ($/MWe/year) | 55000 | 54900 | 54600 | 44000 | 75000 | 43500 | 74500 | D,E | 4,5
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Large Run of River hydro plants are assessed representative between 20MW and 50MW, based on operational projects in Colombia. The central value corresponds to the average value.
B | Aggregated data and fitted curve of Colombian projects in the register by UPME, supplemented with further international sources
C | Assuming ca. 36% share of cost amounting equipment and 64% amounting installation for large scale RoR based on stakeholder input
D | O&M corresponding to 2.2% of CAPEX/year acc. to IEA with an uncertainty range of 2% to 2.5% for large-scale plants according to IRENA
E | Cost are projected with a learning rate approach assuming a 1% learning rate for based on IEA's assumptions in their Global Energy and Climate Model, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values.
F | This is the efficiency of the utilization of the water’s potential energy.
G | Space requirements for new sites is highly uncertain given the geographical dependency. Stakeholder input has resulted in the range that is presented here.
H | Numbers are based on historical operation, but dispatchable hydro plants are not bound by the numbers presented. The theoretical capacity factor is derived by accounting for lower outage times for the upper capacity factor and vice versa.
I | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the limited general technology improvement potential.
J | The baseline cost is derived by economy of scale effects with a proportionality factor of 0.85 based on the cost for large-scale RoR Hydro
References (from column K):
1 | Bloomberg New Energy Finance, Power Asset Database
2 | UPME, “Registro de Proyectos de Generación” database
3 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
4 | IRENA, 2023, Renewable Power Generation Costs in 2022
5 | IEA, 2010, Projected Cost of Generating Electricity
6 | Paratec - Projects that started operation after 2010
7 | Calculation from Sinergox - Data Provided by MME
8 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
9 | U.S. Department of Energy, 2015, “Hydropower Market Report”.
10 | Ramirez-Tovar el al 2022 Land-use in the Electric Colombian System: Hidden Impacts and Risks of Large-scale Renewable Projects. International Journal of Energy Economics and Policy, 12(2),
11 | Discussion with Technology Catalogue stakeholder group
12 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".

## 5.b. Small RoR hydro power
| Technology | Hydro power plant - Medium/small system
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 10 | 10 | 10 | 1 | 20 | 1 | 20 | A | 1,6,11
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | F | 8
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | F | 8
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 9
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 9
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 8
| Construction time (years) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 3,11
| Space requirement (1000 m2/MWe) | 2,4 | 2,4 | 2,4 | 1,4 | 3,2 | 1,4 | 3,2 | G | 10,11
Additional data for non thermal plants
| Capacity factor (%), theoretical | 69.6429 | 69.6429 | 69.6429 | 55.914 | 76.4082 | 55.914 | 76.4082 | H
| Capacity factor (%), incl. outages | 63 | 63 | 63 | 46 | 72 | 46 | 72 | H | 6,7
Ramping configurations
| Ramping (% per minute) | 55 | 55 | 55 | 0 | 100 | 0 | 100 | H | 6,12
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12
| Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0 | 0.5 | 0 | 0.5 |  | 6
| Cold start-up time (hours) | 0.3 | 0.3 | 0.3 | 0 | 0.5 | 0 | 0.5 |  | 6
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 3.02 | 3.0146 | 2.9993 | 2.1 | 3.8 | 2.0856 | 3.7739 | B,E,I,J | 2,3,4,5,11
| - of which equipment | 0.99555 | 0.99377 | 0.98871 | 0.69227 | 1.2527 | 0.68752 | 1.2441 | C,E,I | 2,3,4,11
| - of which installation | 2.0213 | 2.0177 | 2.0074 | 1.4055 | 2.5433 | 1.3959 | 2.5258 | C,E,I | 2,3,4,11
| Fixed O&M ($/MWe/year) | 66500 | 66400 | 66000 | 46200 | 75000 | 45900 | 83000 | D,E | 4,5
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Small Run of River hydro plants are assessed representative between 1MW and 20MW, based on operational projects in Colombia. The central value corresponds to the rounded average value.
B | Aggregated data and fitted curve of Colombian projects in the register by UPME, supplemented with further international sources
C | Assuming ca. 36% share of cost amounting equipment and 64% amounting installation for large scale RoR based on stakeholder input
D | O&M corresponding to 2.2% of CAPEX/year acc. to IEA with an uncertainty range of 2% to 2.5% for small-scale plants according to IRENA
E | Cost are projected with a learning rate approach assuming a 1% learning rate for based on IEA's assumptions in their Global Energy and Climate Model, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values.
F | This is the efficiency of the utilization of the water’s potential energy.
G | Space requirements for new sites is highly uncertain given the geographical dependency. Stakeholder input has resulted in the range that is presented here.
H | Numbers are based on historical operation, but dispatchable hydro plants are not bound by the numbers presented. The theoretical capacity factor is derived by accounting for lower outage times for the upper capacity factor and vice versa.
I | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the limited general technology improvement potential.
J | The baseline cost is derived by economy of scale effects with a proportionality factor of 0.85 based on the cost for large-scale RoR Hydro
References (from column K):
1 | Bloomberg New Energy Finance, Power Asset Database
2 | UPME, “Registro de Proyectos de Generación” database
3 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
4 | IRENA, 2023, Renewable Power Generation Costs in 2022
5 | IEA, 2010, Projected Cost of Generating Electricity
6 | Paratec - Projects that started operation after 2010
7 | Calculation from Sinergox - Data Provided by MME
8 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
9 | U.S. Department of Energy, 2015, “Hydropower Market Report”.
10 | Ramirez-Tovar el al 2022 Land-use in the Electric Colombian System: Hidden Impacts and Risks of Large-scale Renewable Projects. International Journal of Energy Economics and Policy, 12(2),
11 | Discussion with Technology Catalogue stakeholder group
12 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".

## 5.c. Mini RoR hydro power
| Technology | Hydro power plant - Mini/micro system
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | 0.1 | 1 | 0.1 | 1 | A | 1,6,11
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 |  | 8
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 |  | 8
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 9
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 6
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 6
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 |  | 3,11
| Space requirement (1000 m2/MWe) | 2,4 | 2,4 | 2,4 | 1,4 | 3,2 | 1,4 | 3,2 |  | 10,11
Additional data for non thermal plants
| Capacity factor (%), theoretical | 56.3776 | 56.3776 | 56.3776 | 24.3104 | 82.7755 | 24.3104 | 82.7755 | H
| Capacity factor (%), incl. outages | 51 | 51 | 51 | 20 | 78 | 20 | 78 | H | 6,7
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | F
| Minimum load (% of full load) | - | - | - | - | - | - | - | F
| Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0 | 0.5 | 0 | 0.5 |  | 6
| Cold start-up time (hours) | 0.3 | 0.3 | 0.3 | 0 | 0.5 | 0 | 0.5 |  | 6
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 4.2614 | 4.2524 | 4.2307 | 4 | 5 | 3.9712 | 4.964 | B,E,I,J | 2,3,4,5,11
| - of which equipment | 1.4063 | 1.4037 | 1.3966 | 1.3204 | 1.6505 | 1.3114 | 1.6392 | C,E,I | 2,3,4,11
| - of which installation | 2.8551 | 2.85 | 2.8355 | 2.6809 | 3.3511 | 2.6624 | 3.3281 | C,E,I | 2,3,4,11
| Fixed O&M ($/MWe/year) | 94000 | 93600 | 93100 | 80000 | 125000 | 79400 | 124100 | D,E | 4.5
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Mini Run of River hydro plants are assessed representative up to 1MW and below, based on operational projects in Colombia. Mini Run of River hydro plants represent plants suitable for energy communities.
B | Aggregated data and fitted curve of Colombian projects in the register by UPME, supplemented with further international sources
C | Assuming ca. 36% share of cost amounting equipment and 64% amounting installation for large scale RoR based on stakeholder input
D | O&M corresponding to 2.2% of CAPEX/year acc. to IEA with an uncertainty range of 2% to 2.5% for mini-scale plants according to IRENA
E | Cost are projected with a learning rate approach assuming a 1% learning rate for based on IEA's assumptions in their Global Energy and Climate Model, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values.
F | It is assumed that micro and mini hydro are not capable of regulation. The possibility of a turbine bypass could give the possibility of down regulation.
G | Space requirements for new sites is highly uncertain given the geographical dependency. Stakeholder input has resulted in the range that is presented here.
H | Numbers are based on historical operation, but dispatchable hydro plants are not bound by the numbers presented. The theoretical capacity factor is derived by accounting for lower outage times for the upper capacity factor and vice versa.
I | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the limited general technology improvement potential.
J | The baseline cost is derived by economy of scale effects with a proportionality factor of 0.85 based on the cost for large-scale RoR Hydro
References (from column K):
1 | Bloomberg New Energy Finance, Power Asset Database
2 | UPME, “Registro de Proyectos de Generación” database
3 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
4 | IRENA, 2023, Renewable Power Generation Costs in 2022
5 | IEA, 2010, Projected Cost of Generating Electricity
6 | Paratec - Projects that started operation after 2010
7 | Calculation from Sinergox - Data Provided by MME
8 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
9 | U.S. Department of Energy, 2015, “Hydropower Market Report”.
10 | Ramirez-Tovar el al 2022 Land-use in the Electric Colombian System: Hidden Impacts and Risks of Large-scale Renewable Projects. International Journal of Energy Economics and Policy, 12(2),
11 | Discussion with Technology Catalogue stakeholder group
12 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".

## 5.d. Large Hydro reservoir
| Technology | Reservoir hydro power plant
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 200 | 200 | 200 | 50 | 600 | 50 | 600 |  | 1,6,11
| Generating capacity for total power plant (MWe) | 800 | 800 | 800 | 50 | 1250 | 50 | 2400 |  | 1,6,11
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | F | 8
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | F | 8
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 9
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 9
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 8
| Construction time (years) | 5 | 5 | 5 | 4 | 6 | 4 | 6 |  | 3,11
| Space requirement (1000 m2/MWe) | 135,2 | 135,2 | 135,2 | 2,4 | 833,3 | 2,4 | 833,3 | G | 10
Additional data for non thermal plants
| Capacity factor (%), theoretical | 57.483 | 57.483 | 57.483 | 54.6985 | 62.6122 | 54.6985 | 62.6122 | H
| Capacity factor (%), incl. outages | 52 | 52 | 52 | 45 | 59 | 45 | 59 | H | 6,7
Ramping configurations
| Ramping (% per minute) | 12 | 12 | 12 | 6 | 23 | 6 | 23 |  | 6,12
| Minimum load (% of full load) | 48 | 48 | 48 | 44 | 51 | 44 | 51 |  | 12
| Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0 | 0.5 | 0 | 0.5 |  | 6
| Cold start-up time (hours) | 2 | 2 | 2 | 0.1 | 7 | 0.1 | 7 |  | 6
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2.5 | 2.4955 | 2.4828 | 1.85 | 3.2 | 1.8373 | 3.178 | B,E,I,J | 2,3,4,5,11
| - of which equipment | 1.25 | 1.2478 | 1.2414 | 0.925 | 1.6 | 0.91864 | 1.589 | C,E,I | 2,3,4,11
| - of which installation | 1.25 | 1.2478 | 1.2414 | 0.925 | 1.6 | 0.91864 | 1.589 | C,E,I | 2,3,4,11
| Fixed O&M ($/MWe/year) | 55000 | 54900 | 54600 | 37000 | 80000 | 36700 | 79500 | D,E | 4,5
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes (from column J):
A | Capacity corresponds to the median, lower and higher bound of the operational hydro reservoir power plants in Colombia. The higher uncertainty interval in 2050 corresponds to the largest reservoir plant currently in planning phase.
B | Aggregated data and fitted curve of Colombian projects in the register by UPME, supplemented with further international sources
C | Assuming ca. 50 % share of cost amounting equipment and 50% amounting installation for large scale reservoir plants according to IRENA Renewable Power Generation Cost in 2022
D | O&M corresponding to 2.2 % of CAPEX/year acc. to IEA with an uncertainty range of 2 % to 2.5 % for large-scale plants according to IRENA
E | Cost are projected with a learning rate approach assuming a 1 % learning rate for based on IEA's assumptions in their Global Energy and Climate Model, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values.
F | This is the efficiency of the utilization of the water’s potential energy
G | Space requirements for new sites is highly uncertain given the geographical dependency.
H | Numbers are based on historical operation, but dispatchable hydro plants are not bound by the numbers presented. The theoretical capacity factor is derived by accounting for lower outage times for the upper capacity factor and vice versa.
I | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the limited general technology improvement potential.
J | The baseline cost corresponds to stakeholder consultation and the presented international benchmark data
References (from column K):
1 | Bloomberg New Energy Finance, Power Asset Database
2 | UPME, “Registro de Proyectos de Generación” database
3 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
4 | IRENA, 2023, Renewable Power Generation Costs in 2022
5 | IEA, 2010, Projected Cost of Generating Electricity
6 | Paratec - Projects that started operation after 2010
7 | Calculation from Sinergox - Data Provided by MME
8 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
9 | U.S. Department of Energy, 2015, “Hydropower Market Report”.
10 | Ramirez-Tovar el al 2022 Land-use in the Electric Colombian System: Hidden Impacts and Risks of Large-scale Renewable Projects. International Journal of Energy Economics and Policy, 12(2),
11 | Discussion with Technology Catalogue stakeholder group
12 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".

## 6.a. Geothermal large
| Technology | Geothermal power plant (flash or dry)
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 50 | 50 | 50 | 30 | 500 | 30 | 500 | A | 1,4,5,9
| Generating capacity for total power plant (MWe) | 100 | 100 | 100 | 30 | 500 | 30 | 500 | A | 1,4,5,9
| Electricity efficiency, net (%), name plate | 16% | 17% | 18% | 8% | 18% | 10% | 20% |  | 6
| Electricity efficiency, net (%), annual average | 15% | 16% | 17% | 8% | 18% | 10% | 20% |  | 6
| Forced outage (%) | 10% | 10% | 10% | 5% | 30% | 5% | 30% |  | 4
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 4
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 4,7,9
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 | E | 4,7,9
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 4
Additional data for non thermal plants
| Capacity factor (%), theoretical | 88% | 88% | 88% | 70% | 100% | 70% | 100% | J,K | 4,9
| Capacity factor (%), incl. outages | 73.11% | 73.11% | 73.11% | 43.35% | 91.35% | 43.35% | 91.35% | J,K | 4
Ramping configurations
| Ramping (% per minute) | 3% | 10% | 20% | - | - | - | - |  | 8
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | F
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | F
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | F
| CH4 (g per GJ fuel) | - | - | - | - | - | - | - | F
| N2O (g per GJ fuel) | - | - | - | - | - | - | - | F
Financial data
| Nominal investment (M$/MWe) | 4.7185 | 4.4447 | 4.1021 | 3.2832 | 6.1487 | 2.8544 | 5.3456 | B,C,M,P | 2,3,4,9
| - of which equipment (%) | 60% | 60% | 60% | 40% | 70% | 40% | 70% | G,M | 2,4
| - of which installation (%) | 40% | 40% | 40% | 30% | 50% | 30% | 50% | G,M | 2,4
| Fixed O&M ($/MWe/year) | 89800 | 84600 | 78100 | 45900 | 137600 | 39900 | 119700 | L,M,N,P | 2,4,9
| Variable O&M ($/MWh) | 0.30356 | 0.28594 | 0.2639 | 0.22486 | 0.38226 | 0.19549 | 0.33232 | M,P | 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Exploration costs (M$/MWe) | 0.65519 | 0.65519 | 0.61424 | 0.45863 | 0.85174 | 0.42997 | 0.79851 | H,O | 4,9
| Capacity expansion cost of nominal investment (%) | 81.53% | 81.53% | 81.53% | 90.68% | 73.37% | 90.68% | 73.37% | I | 9
Notes (from column J):
A | Geothermal plants (flash or dry) are assessed representative between 30 MW and 500 MW in 2024, based on operational projects in Colombia and in alignment with further international sources.
B | Investment cost are excluding Exploration costs (see under Technology specific data).
C | Investment cost include project review and planning, field development, construction, start-up and commissioning and other unforeseen costs.
D | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in efficiency will give a lower investment cost per MW. These large units are assumed to be flash units at high source temperatures.
E | Refers to construction of the steam cycle power plant itself. Preparation of the geothermal site includes surveying, exploration, drilling, resource confirmation, which can take 4-5 years in total.
F | Geothermal do emit H2S.
G | Assumed 60 % equipment, 40 % installation based on international data.
H | Exploration cost includes preliminary survey, adaptation, road works, platform design and planning, exploratory studies, exploratory drilling, reservoir testing and modelling, administration and unforeseen costs in exploratory phases for 50 MW projects in Colombia. This cost varies significantly as it depends on the site's characteristics, regulatory requirements, and market conditions and should therefore be considered on plant level.
I | Installing new capacity (MW) in a new phase for an existing project.
J | Based on operational data from Colombia.
K | Assumed the same theoretical capacity factor for 2030 and 2050 and calculated the capacity factor incl. outages based on the reduction of outages.
L | Based on the base scenario (scenario 2) in reference [9].
M | Cost are projected with a learning rate approach assuming a 5% learning rate for both equipment and installation based on IEA's World Energy Outlook 2023, and 5% for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges used for the central values.
N | Total O&M cost from reference [9] excluding cost for variable O&M from reference [4].
O | Uncertainty (Upper/Lower) is estimated as +/- 30 %
P | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the general technology improvement potential.
References (from column K):
1 | UPME, “Registro de Proyectos de Generación” database
2 | Learning curve approach for the development of financial parameters.
3 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
4 | Danish Energy Agency, Ea Energy Analyses, 2024, Technology Data for the Indonesian Power Sector
5 | Discussion with Technolgy Catalogue stakeholder group
6 | Moon & Zarrouk, 2012, “Efficiency of Geothermal Power Plants: A Worldwide Review”.
7 | Moore, 2016, "Geothermal Power Generation: Developments and Innovation, chapter 18: Project permitting, finance, and economics for geothermal power generation"
8 | Geothermal Energy Association, 2015, "Geothermal Energy Association Issue Brief: Firm and Flexible Power Services Available from Geothermal Facilities"
9 | K&M Advisor a Dorado Group Company. (2020). "Evaluación preliminar de la factibilidad económica y financiera de proyectos de geotermia en Colombia. Informe final”

## 6.b. Geothermal small
| Technology | Geothermal power plant (binary or condensing)
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 10 | 10 | 10 | 1 | 50 | 1 | 50 | A | 1,4,5,9
| Generating capacity for total power plant (MWe) | 20 | 20 | 20 | 5 | 50 | 5 | 130 | A | 1,4,5,9
| Electricity efficiency, net (%), name plate | 10% | 11% | 12% | 6% | 12% | 8% | 14% | D | 6
| Electricity efficiency, net (%), annual average | 10% | 11% | 12% | 6% | 12% | 8% | 14% | D | 6
| Forced outage (%) | 10% | 10% | 10% | 5% | 30% | 5% | 30% |  | 4
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 4
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 4,7,9
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 | E | 4,7,9
| Space requirement (1000 m2/MWe) | 30 | 31 | 32 | 20 | 40 | 20 | 40 |  | 4
Additional data for non thermal plants
| Capacity factor (%), theoretical | 88% | 88% | 88% | 70% | 100% | 70% | 100% | J,K | 4,9
| Capacity factor (%), incl. outages | 73.11% | 73.11% | 73.11% | 43.35% | 91.35% | 43.35% | 91.35% | J,K | 4
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | -
| Minimum load (% of full load) | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | F
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | F
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | F
| CH4 (g per GJ fuel) | - | - | - | - | - | - | - | F
| N2O (g per GJ fuel) | - | - | - | - | - | - | - | F
Financial data
| Nominal investment (M$/MWe) | 6.0037 | 5.6553 | 5.2195 | 4.5983 | 7.6339 | 3.9977 | 6.6367 | B,C,M,P | 2,3,4,9
| - of which equipment (%) | 60% | 60% | 60% | 40% | 70% | 40% | 70% | G,M | 2,4
| - of which installation (%) | 40% | 40% | 40% | 30% | 50% | 30% | 50% | G,M | 2,4
| Fixed O&M ($/MWe/year) | 88900 | 83700 | 77300 | 45900 | 137600 | 39900 | 119600 | L,M,N,P | 2,4,9
| Variable O&M ($/MWh) | 0.43847 | 0.41303 | 0.3812 | 0.32885 | 0.54809 | 0.2859 | 0.47649 | M,P | 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Exploration costs (M$/MWe) | 2.98 | 2.98 | 2.7938 | 2.086 | 3.874 | 1.9556 | 3.6319 | H,O | 4,9
| Capacity expansion cost of nominal investment (%) | 68.9% | 68.9% | 68.9% | 76.68% | 62.05% | 76.68% | 62.05% | I,Q | 9
Notes (from column J):
A | Geothermal plants (binary or condensing) are assessed representative between 1 MW and 50 MW in 2024, based on operational projects in Colombia and in alignment with further international sources.
B | Investment cost are excluding Exploration costs (see under Technology specific data).
C | Investment cost include project review and planning, field development, construction, start-up and commissioning and other unforeseen costs.
D | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in efficiency will give a lower investment cost per MW. These smaller units are assumed to be binary units at medium source temperatures.
E | Refers to construction of the steam cycle power plant itself. Preparation of the geothermal site includes surveying, exploration, drilling, resource confirmation, which can take 4-5 years in total.
F | Geothermal do emit H2S.
G | Assumed 60 % equipment, 40 % installation based on international data
H | Exploration cost includes preliminary survey, adaptation, road works, platform design and planning, exploratory studies, exploratory drilling, reservoir testing and modelling, administration and unforeseen costs in exploratory phases for 50 MW projects in Colombia. This cost varies significantly as it depends on the site's characteristics, regulatory requirements, and market conditions and should therefore be considered on plant level.
I | Installing new capacity (MW) in a new phase for an existing project.
J | Based on operational data from Colombia.
K | Assumed the same theoretical capacity factor for 2030 and 2050, and calculated the capacity factor “incl. outages” based on the impact of outages themselves.
L | Based on the base scenario (scenario 2) in reference 9.
M | Cost are projected with a learning rate approach assuming a 5% learning rate for both equipment and installation based on IEA's World Energy Outlook 2023, and 5% for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges used for the central values.
N | Total O&M cost [9] excluding cost for variable O&M.
O | Uncertainty (Upper/Lower) is estimated as +/- 30 %
P | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the general technology improvement potential.
Q | Assumed same percentage for uncertainty as geothermal flash.
References (from column K):
1 | UPME, “Registro de Proyectos de Generación” database
2 | Learning curve approach for the development of financial parameters.
3 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
4 | Danish Energy Agency, Ea Energy Analyses, 2024, Technology Data for the Indonesian Power Sector
5 | Discussion with Technology Catalogue stakeholder group
6 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
7 | Moore, 2016, "Geothermal Power Generation: Developments and Innovation, chapter 18: Project permitting, finance, and economics for geothermal power generation"
8 | Geothermal Energy Association, 2015, "Geothermal Energy Association Issue Brief: Firm and Flexible Power Services Available from Geothermal Facilities"
9 | K&M Advisor a Dorado Group Company. (2020). "Evaluación preliminar de la factibilidad económica y financiera de proyectos de geotermia en Colombia. Informe final”

## 7. Biomass power plant
| Technology | Biomass power plant (palm oil / sugar cane / rice husk)
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,4,9
| Generating capacity for total power plant (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,4,9
| Electricity efficiency, net (%), name plate | 32% | 32% | 32% | 25% | 35% | 25% | 35% |  | 1,5,6
| Electricity efficiency, net (%), annual average | 31% | 31% | 31% | 25% | 35% | 25% | 35% |  | 1,5,6
| Forced outage (%) | 7% | 7% | 7% | 5.25% | 8.75% | 5.25% | 8.75% | B | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 4.5 | 7.5 | 4.5 | 7.5 | B | 1
| Technical lifetime (years) | 25 | 25 | 25 | 18.75 | 31.25 | 18.75 | 31.25 | B | 1,6
| Construction time (years) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | B | 6
| Space requirement (1000 m2/MWe) | 35 | 35 | 35 | 26.25 | 43.75 | 26.25 | 43.75 | B | 1,7
Additional data for non thermal plants
| Capacity factor (%), theoretical | 52.57% | 52.57% | 52.57% | 7.427% | 83.3% | 7.427% | 83.3% | D,E | 2,3
| Capacity factor (%), incl. outages | 43.25% | 43.25% | 43.25% | 5.8% | 72.1% | 5.8% | 72.1% | D,E | 2,3
Ramping configurations
| Ramping (% per minute) | 10% | 10% | 10% | [5 empty] | 5
| Minimum load (% of full load) | 30% | 30% | 30% | [5 empty] | 5
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 5
| Cold start-up time (hours) | 10 | 10 | 10 | [5 empty] | 5
Environment
| PM 2.5 (mg per Nm3) | 12.5 | 12.5 | 12.5 | [5 empty] | 5
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [5 empty] | 5
| NOX (g per GJ fuel) | 125 | 125 | 125 | [5 empty] | 5
| CH4 (g per GJ fuel) | 30 | 30 | 30 | 10 | 100 | 10 | 100 | H | 10
| N2O (g per GJ fuel) | 4 | 4 | 4 | 1.5 | 15 | 1.5 | 15 | I | 10
Financial data
| Nominal investment (M$/MWe) | 2.5634 | 2.466 | 2.3192 | 1.6639 | 2.8894 | 1.5054 | 2.6142 | A,C,F,G,J | 1
| - of which equipment (%) | 65% | 65% | 65% | 50% | 85% | 50% | 85% | A | 1
| - of which installation (%) | 35% | 35% | 35% | 15% | 50% | 15% | 50% | A | 1
| Fixed O&M ($/MWe/year) | 60700 | 58400 | 54900 | 48300 | 80900 | 43700 | 73200 | A,F,G,J | 1
| Variable O&M ($/MWh) | 3.8226 | 3.6774 | 3.4585 | 2.8669 | 4.7782 | 2.5938 | 4.3231 | A,F,G,J | 1
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Notes (from column J):
A | Based on prices from countries with similar biomass input
B | Uncertainty (Upper/Lower) is estimated as +/- 25 %.
C | Land cost for planting biomass is not included
D | The capacity factor is calculated with available information.
E | Assumed the same theoretical capacity factor for 2030 and 2050 and changed the capacity factor incl. outages based on the reduction of outages.
F | The values for the Stated Policies Scenario (lower scenario normally used as estimate for lower uncertainty) and Announced Pledges Scenario (median scenario normally used as central estimate) from IEA has been switched around because of the way IEA projects bioenergy and the values for the median scenario (central estimate) is lower than the values for the lower scenario (lower uncertainty).
G | Cost are projected with a learning rate approach assuming a 5% learning rate for both equipment and installation based on IEA's World Energy Outlook 2023, and 5% for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges used for the central values.
H | Data from existing projects in Colombia [3] shows much higher numbers with a central estimate at 600 g/GJ and a range between 130 - 2809 g/GJ.
I | Data from existing projects in Colombia [3] shows much higher numbers with a central estimate at 79.9 g/GJ and a range between 17.2 - 374.5 g/GJ.
J | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the general technology improvement potential.
References (from column K):
1 | Danish Energy Agency, Ea Energy Analyses, 2024, Technology Data for the Indonesian Power Sector
2 | XM: Paratec
3 | Data from Sinergox - calculation provided by Emergente
4 | IFC and BMF, 2017, "Converting biomass to energy - A guide for developers and investors".
5 | Danish Energy Agency and COWI, 2017, "Technology catalogue for biomass to energy".
6 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
7 | India Central Electricity Authority, 2007, "Report on the Land Requirement of Thermal Power Stations".
8 | Bilateral meetings with stakeholders
9 | Danish Energy Agency, Ea Energy Analyses, 2023, Viet Nam Technology Catalogue for Power Generation
10 | IPCC Guidelines for National Greenhouse Gas Inventories, 2006

## 8. Biogas power plant
| Technology | Biogas power plant
|  | 2023 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 0.88 | 0.88 | 0.88 | 0.25 | 1.9 | 0.25 | 1.9 |  | 10
| Generating capacity for total power plant (MWe) | 0.88 | 0.88 | 0.88 | 0.25 | 1.9 | 0.25 | 1.9 |  | 10
| Electricity efficiency, net (%), name plate | 42% | 42% | 42% | 41% | 42.5% | 41% | 42.5% |  | 10
| Electricity efficiency, net (%), annual average | 40% | 40% | 40% | 35% | 41% | 35% | 41% | E | 1,2,3
| Forced outage (%) | 10% | 10% | 10% | 9% | 12% | 9% | 12% |  | 9
| Planned outage (weeks per year) | 3 | 3 | 3 | 1 | 5 | 1 | 5 |  | 9
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 50 | 20 | 50 |  | 9
| Construction time (years) | 1.5 | 1.5 | 1.5 | 0.5 | 2 | 0.5 | 2 |  | 9
| Space requirement (1000 m2/MWe) | 0.649 | 0.649 | 0.649 | 0.453 | 0.845 | 0.453 | 0.845 |  | 9
Additional data for non thermal plants
| Capacity factor (%), theoretical | 8.188% | 8.188% | 8.188% | 2.723% | 13.14% | 2.723% | 13.14% | A,B | 8
| Capacity factor (%), incl. outages | 6.944% | 6.944% | 6.944% | 2.166% | 11.72% | 2.166% | 11.72% | A | 8
Ramping configurations
| Ramping (% per minute) | 20% | 20% | 20% | 10% | 30% | 10% | 30% |  | 5
| Minimum load (% of full load) | 40% | 30% | 15% | 30% | 50% | 10% | 20% |  | 6
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| CH4 (g per GJ fuel) | 1 | 1 | 1 | 0,3 | 3 | 0,3 | 3 |  | 11
| N2O (g per GJ fuel) | 0,1 | 0,1 | 0,1 | 0,03 | 0,3 | 0,03 | 0,3 |  | 11
Financial data
| Nominal investment (M$/MWe) | 4.38 | 4.2136 | 3.9628 | 3.12 | 5.01 | 2.8228 | 4.5328 | C,D,F | 10
| - of which equipment (%) | 81% | 81% | 81% | 79% | 87% | 79% | 87% | D | 10
| - of which installation (%) | 19% | 19% | 19% | 13% | 21% | 13% | 21% | D | 10
| Fixed O&M ($/MWe/year) | 46200 | 44400 | 41800 | 42700 | 53800 | 38600 | 48700 | C,D,F | 10
| Variable O&M ($/MWh) | 0.018 | 0.017316 | 0.016285 | 0.016 | 0.019 | 0.014476 | 0.01719 | C,D,F | 10
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10
Notes (from column J):
A | The capacity factor is calculated with available information.
B | Assumed the same theoretical capacity factor for 2030 and 2050
C | The values for the Stated Policies Scenario (lower scenario normally used as estimate for lower uncertainty) and Announced Pledges Scenario (median scenario normally used as central estimate) from IEA has been switched around because of the way IEA project bioenergy.
D | Cost are projected with a learning rate approach assuming a 5 % learning rate for both equipment and installation based on IEA's World Energy Outlook 2023, and 5 % for O&M, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges used for the central values.
E | Assumed same percental difference to Electricity efficiency (net, name plate) as international TC's
F | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the general technology improvement potential.
References (from column K):
1 | Danish Energy Agency, Ea Energy Analyses, 2024, Technology Data for the Indonesian Power Sector
2 | Danish Energy Agency, Ea Energy Analyses, 2023, Viet Nam Technology Catalogue for Power Generation
3 | Danish Energy Agency, Technology Catalogue for Generation of Electricity and District Heating, 2024
4 | XM: Paratec
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
7 | Winrock, 2015, "Buku Panduan Konversi POME Menjadi Biogas, Pengembangan Proyek di Indonesia", USAID – Winrock International.
8 | Data from Sinergox - calculation provided by Emergente
9 | Discussion with Technology Catalogue stakeholder group
10 | Bilateral meetings with stakeholders
11 | IPCC Guidelines for National Greenhouse Gas Inventories, 2006

## 9. Coal Supercritical
| Technology | Supercritical coal power plant
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 201 | 201 | 201 | 164 | 270 | 164 | 270 |  | 4
| Generating capacity for total power plant (MWe) | 201 | 201 | 201 | 170 | 434 | 170 | 434 |  | 4
| Electricity efficiency, net (%), name plate | 38% | 39% | 40% | 33% | 40% | 35% | 42% |  | 2
| Electricity efficiency, net (%), annual average | 37% | 38% | 39% | 33% | 40% | 35% | 42% |  | 2
| Forced outage (%) | 7% | 6% | 3% | 5% | 15% | 2% | 7% | F | 2
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | F | 2
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 2
| Construction time (years) | 4 | 3 | 3 | 3 | 5 | 2 | 4 | F | 2
| Space requirement (1000 m2/MWe) | 1.83 | 1.83 | 1.83 | 0.95193 | 2.7285 | 0.95193 | 2.7285 |  | 6
Additional data for non thermal plants
| Capacity factor (%), theoretical | 44.51% | 44.51% | 44.51% | 26.46% | 60.03% | 26.46% | 60.03% | C,H,I | 5
| Capacity factor (%), incl. outages | 35.82% | 37.81% | 40.68% | 19.03% | 53.74% | 22.71% | 56.57% | C,H | 5
Ramping configurations
| Ramping (% of Full Load/Minute) | 4% | 4% | 4% | 3% | 4% | 3% | 4% | J | 2.4
| Minimum load (% of full load) | 47% | 25% | 20% | 39% | 55% | 20% | 40% | F | 4
| Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | D | 4
| Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 15 | D | 4
| Minimum Up time (hours) | 6 | 6 | 6 |  |  |  |  | K,L | 9
| Minimum Down time (hours) | 4 | 4 | 4 |  |  |  |  | K,L | 9
Environment
| PM 2.5 (g/GJ) | 3.4 | 3.4 | 3.4 | [5 empty] | 8
| SO2 (g/GJ of fuel input) | 3101.7541 | 3101.7541 | 3101.7541 | [5 empty] | 8
| NOX (g per GJ fuel) | 209 | 209 | 209 | 209 | 209 | 209 | 209 |  | 8
| CH4 (g per GJ fuel) | 3.2721 | 3.2721 | 3.2721 | 1.8347 | 7.0617 | 1.8347 | 7.0617 |  | 5
| N2O (g per GJ fuel) | 4.9127 | 4.9127 | 4.9127 | 2.7518 | 10.5995 | 2.7518 | 10.5995 |  | 5
Financial data
| Nominal investment (M$/MWe) | 1.7988 | 1.7774 | 1.7076 | 1.1158 | 2.2274 | 1.0592 | 2.1144 | A,B,M | 1,2,3,10
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 50500 | 49900 | 47900 | 37900 | 63100 | 35900 | 59900 | A,B,G | 1,2,3
| Variable O&M ($/MWh) | 1.2611 | 1.246 | 1.1971 | 0.9458 | 1.5763 | 0.89783 | 1.4964 | A,B,G | 1,2,3
| Start-up costs ($/MWe/start-up) | 64.084 | 64.084 | 64.084 | 48.063 | 80.105 | 48.063 | 80.105 | A,B,G | 2
Notes (from column J):
A | Based on international data.
B | Assuming that cost fall 0.2 % each year.
C | The capacity factor in 2024 is calculated from 2017-2024 for each plant with available information.
D | Estimation based on international data for the capability of the machine. An average of the operational data in Colombia [4] shows that hot start-up time is 8 hours, warm start-up time is 36 hours and cold start-up time is 65 hours. The operational data from Colombia is higher than international data because of the design of the Colombian energy system.
E | This is for programmed stops, for non-programmed stops the time ranges between 0 and 1 h.
F | Assumed gradual improvement to international standard in 2050.
G | Uncertainty (Upper/Lower) is estimated as +/- 25 % in this case, to account for the variability and uncertainties inherent in its estimation.
H | Assumed the same theoretical capacity factor for 2030 and 2050 and changed the capacity factor incl. outages based on the reduction of outages.
I | Uncertainties for 2050 have been assumed to be the same as in 2030.
J | Assumed no improvement for regulatory capability.
K | Estimation based on international data for the capability of the machine. An average of the operational data in Colombia [4] shows that minimum up time is 48 hours and minimum down time is 18,67 hours (for programmed stops, for non-programmed stops the time for down time ranges between 0 and 1 hours). The operational data from Colombia is a lot higher than international data because of the design of the Colombian energy system.
L | Coal is less flexible than gas regarding minimum up/down time.
M | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the general technology improvement potential.
References (from column K):
1 | Danish Energy Agency, Technology Catalogue for Generation of Electricity and District Heating, 2024
2 | Danish Energy Agency, Ea Energy Analyses, 2024, Technology Data for the Indonesian Power Sector
3 | Danish Energy Agency, Ea Energy Analyses, 2023, Viet Nam Technology Catalogue for Power Generation
4 | XM: Data From Paratec - Projects from 2010 on (3 units for Coal)
5 | Data from Sinergox - calculation provided by Emergente
6 | Ramirez-Tovar, A., Moreno-Chuquen, R., & Moreno-Quintero, R. (2022). Land-use in the Electric Colombian System: Hidden Impacts and Risks of Large-scale Renewable Projects. International Journal of Energy Economics and Policy, 12(2), 127–134. https://doi.org/10.32479/ijeep.11631
7 | Bilateral meetings with stakeholders
8 | Institute of Hydrology, Meteorology and Environmental Studies (IDEAM), 2022, Informe del inventario nacional de gases efecto invernadero 1990-2018 y carbono negro 2010-2018 de Colombia - Tercer Informe Bienal de Actualización de Cambio Climático de Colombia
9 | Danish Energy Agency, Ea Energy Analyses, 2022, Technology Data for the Indian Power Sector
10 | IEA, 2023, World Energy Outlook Global Energy and Climate Model input data

## 10. CCGT (GAS)
| Technology | Combined Cycle Gas Turbine
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 377 | 377 | 377 | 239 | 555 | 239 | 555 |  | 5
| Generating capacity for total power plant (MWe) | 377 | 377 | 377 | 239 | 555 | 239 | 555 |  | 5
| Electricity efficiency, net (%), name plate | 57% | 60% | 61% | 45% | 62% | 55% | 65% |  | 3.6
| Electricity efficiency, net (%), annual average | 56% | 59% | 60% | 39% | 61% | 54% | 64% |  | 3
| Forced outage (%) | 5% | 5% | 5% | 3% | 10% | 3% | 10% |  | 3
| Planned outage (weeks per year) | 5 | 5 | 5 | 3 | 8 | 3 | 8 |  | 3
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 3
| Space requirement (1000 m2/MWe) | 1.3 | 1.3 | 1.3 | 1.16 | 1.41 | 1.16 | 1.41 |  | 8
Additional data for non thermal plants
| Capacity factor (%), theoretical | 34.18% | 34.18% | 34.18% | 1.934% | 55.33% | 1.934% | 55.33% | C | 7
| Capacity factor (%), incl. outages | 29.35% | 29.35% | 29.35% | 1.473% | 50.58% | 1.473% | 50.58% | D | 7
Ramping configurations
| Ramping (% per minute) | 20% | 20% | 20% | 10% | 30% | 10% | 30% | G | 3
| Minimum load (% of full load) | 45% | 30% | 15% | 24% | 70% | 10% | 40% | I | 3,5,6
| Warm start-up time (hours) | 2 | 1 | 1 | 1 | 3 | 0.5 | 2 | E,I | 1,3,6
| Cold start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | E | 1,3,6
| Minimum Up time (hours) | 4 | 4 | 4 |  |  |  |  | K,L | 11
| Minimum Down time (hours) | 3 | 3 | 3 |  |  |  |  | K,L | 11
Environment
| PM 2.5 (g/GJ) | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 |  | 10
| SO2 (g/GJ) | 0.281 | 0.281 | 0.281 |  |  |  |  | J | 10
| NOX (g per GJ fuel) | 89 | 60 | 20 | 20 | 89 | 20 | 89 | I | 3,4,10
| CH4 (g per GJ fuel) | 1.7872 | 1.7872 | 1.7872 | 0.52909 | 2.3415 | 0.52909 | 2.3415 |  | 7
| N2O (g per GJ fuel) | 0.17972 | 0.17972 | 0.17972 | 0.053342 | 0.23846 | 0.053342 | 0.23846 |  | 7
Financial data
| Nominal investment (M$/MWe) | 1.1048 | 1.0916 | 1.0488 | 0.64199 | 1.3625 | 0.60943 | 1.2934 | A,B,M | 1,2,3,4
| - of which equipment (%) | 50% | 50% | 50% | 50% | 50% | 50% | 50% | A,B | 1,3,4
| - of which installation (%) | 50% | 50% | 50% | 50% | 50% | 50% | 50% | A,B | 1,3,4
| Fixed O&M ($/MWe/year) | 32900 | 32500 | 31200 | 24700 | 41100 | 23400 | 39000 | A,B,H | 1,3,4
| Variable O&M ($/MWh) | 1.7353 | 1.7146 | 1.6473 | 1.3015 | 2.1691 | 1.2355 | 2.0591 | A,B,H | 1,3,4
| Start-up costs ($/MWe/start-up) | 92.8402 | 92.8402 | 92.8402 | 69.6302 | 116.0503 | 69.6302 | 116.0503 | H | 3.4
Notes (from column J):
A | Based on aggregated data of Colombian projects in the register database by UPME (projects from 2018 and forward), supplemented with further prices from international sources.
B | Assuming that cost fall 0.2 % each year.
C | Calculated based on the parameters: Capacity factor incl. outages, Forced outage and Planned outage.
D | The capacity factor is calculated from 2017-2024 for each plant with available information.
E | Estimation based on international data for the capability of the machine. An average of the operational data in Colombia [5] shows that hot start-up time is 16,5 hours, warm start-up time is 28 hours and cold start-up time is 46,5 hours. The operational data from Colombia is higher than international data because of the design of the Colombian energy system.
F | This is for programmed stops, for non-programmed stops the time ranges between 0 and 1 hour.
G | Assumed no improvement for regulatory capability.
H | Uncertainty (Upper/Lower) is estimated as +/- 25 %.
I | Assumed gradual improvement to international standard in 2050.
J | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
K | Estimation based on international data for the capability of the machine. An average of the operational data in Colombia [5] shows that minimum up time is 9,08 hours and minimum down time is 4 hours (for programmed stops, for non-programmed stops the time for down time ranges between 0 and 1 hours). The operational data from Colombia is higher than international data because of the design of the Colombian energy system.
L | Gas is more flexible than coal regarding minimum up/down time
M | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the general technology improvement potential.
References (from column K):
1 | Danish Energy Agency, Technology Catalogue for Generation of Electricity and District Heating, 2024
2 | UPME, 2024, “Registro de Proyectos de Generación” database
3 | Danish Energy Agency, Ea Energy Analyses, 2024, Technology Data for the Indonesian Power Sector
4 | Danish Energy Agency, Ea Energy Analyses, 2023, Viet Nam Technology Catalogue for Power Generation
5 | XM: Data from Paratec - Projects from 2010 on (4 units for CCGT)
6 | Siemens, 2010, "Flexible future for combined cycle".
7 | Data from Sinergox - calculation provided by Emergente
8 | Ramirez-Tovar, A., Moreno-Chuquen, R., & Moreno-Quintero, R. (2022). Land-use in the Electric Colombian System: Hidden Impacts and Risks of Large-scale Renewable Projects. International Journal of Energy Economics and Policy, 12(2), 127–134. https://doi.org/10.32479/ijeep.11631
9 | Bilateral meetings with stakeholders
10 | Institute of Hydrology, Meteorology and Environmental Studies (IDEAM), Informe del inventario nacional de gases efecto invernadero 1990-2018 y carbono negro 2010-2018 de Colombia - Tercer Informe Bienal de Actualización de Cambio Climático de Colombia
11 | Danish Energy Agency, Ea Energy Analyses, 2022, Technology Data for the Indian Power Sector

## 11. SCGT (GAS)
| Technology | Simple Cycle Gas Turbine - large system
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 65.5 | 65.5 | 65.5 | 8 | 200 | 8 | 200 |  | 6
| Generating capacity for total power plant (MWe) | 131 | 131 | 131 | 50 | 200 | 50 | 200 |  | 6
| Electricity efficiency, net (%), name plate | 34% | 36% | 40% | 26.86% | 37.06% | 36% | 42.8% | J | 3.8
| Electricity efficiency, net (%), annual average | 33% | 35% | 39% | 23.1% | 38.15% | 35.1% | 41.73% | J | 3
| Forced outage (%) | 2% | 2% | 2% | 1% | 3% | 1% | 3% | K | 1.3
| Planned outage (weeks per year) | 3 | 3 | 3 | 1.4744 | 5 | 1.4744 | 5 | K | 1.3
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 | I | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.125 | 1.875 | 1.125 | 1.875 | F | 1, 3
| Space requirement (1000 m2/MWe) | 2.01 | 2.01 | 2.01 | 1.13 | 3.5 | 1.13 | 3.5 |  | 7
Additional data for non thermal plants
| Capacity factor (%), theoretical | 57.02% | 57.02% | 57.02% | 6.595% | 100% | 6.595% | 100% | H | 5
| Capacity factor (%), incl. outages | 52.65% | 52.65% | 52.65% | 5.782% | 96.19% | 5.782% | 96.19% | C | 5
Ramping configurations
| Ramping (% per minute) | 20% | 20% | 20% | 10% | 30% | 10% | 30% | G | 1,3,9
| Minimum load (% of full load) | 55% | 30% | 15% | 24% | 78% | 10% | 40% | L | 3,4,6
| Warm start-up time (hours) | 0.23 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.4 | D | 1,3,4
| Cold start-up time (hours) | 0,5 | 0,5 | 0,5 | 0.4 | 1 | 0.4 | 1 | D | 1,3,4
| Minimum Up time (hours) | 4 | 4 | 4 |  |  |  |  | E,N | 11
| Minimum Down time (hours) | 3 | 3 | 3 |  |  |  |  | E,N | 11
Environment
| PM 2.5 (g/GJ) | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 |  | 10
| SO2 (g/GJ) | 0.281 | 0.281 | 0.281 |  |  |  |  | M | 10
| NOX (g per GJ fuel) | 89 | 60 | 20 | 20 | 89 | 20 | 89 | L | 3,4,10
| CH4 (g per GJ fuel) | 2.3506 | 2.3506 | 2.3506 | 0.00020822 | 4.7561 | 0.00020822 | 4.7561 |  | 5
| N2O (g per GJ fuel) | 0.24881 | 0.24881 | 0.24881 | 0.00060313 | 0.47369 | 0.00060313 | 0.47369 |  | 5
Financial data
| Nominal investment (M$/MWe) | 0.97387 | 0.96224 | 0.92447 | 0.70592 | 1.5361 | 0.67012 | 1.4582 | A,B,O | 1,2,3,4
| - of which equipment (%) | 50% | 50% | 50% | 50% | 50% | 50% | 50% | A,B | 1,2,3,4
| - of which installation (%) | 50% | 50% | 50% | 50% | 50% | 50% | 50% | A,B | 1,2,3,4
| Fixed O&M ($/MWe/year) | 29400 | 29000 | 27900 | 22100 | 36800 | 20900 | 34900 | A,B,F | 1,3,4,8
| Variable O&M ($/MWh) | 5.5196 | 5.4537 | 5.2397 | 4.1397 | 6.8995 | 3.9298 | 6.5496 | A,B,F | 1,3,4,8
| Start-up costs ($/MWe/start-up) | 29.2178 | 29.2178 | 29.2178 | 21.9134 | 36.5223 | 21.9134 | 36.5223 | F | 3.4
Notes (from column J):
A | Based on aggregated data of Colombian projects in the register database by UPME, supplemented with further international sources prices from international sources
B | Assuming that cost fall 0.2 % each year
C | The capacity factor is calculated from 2017-2024 for each plant with available information.
D | Estimation based on international data for the capability of the machine. An average of the operational data in Colombia [6] shows that hot start-up time is 5,35 hours, warm start-up time is 11,25 hours and cold start-up time is 17 hours. The operational data from Colombia is higher than international data because of the design of the Colombian energy system.
E | Gas is more flexible than coal regarding minimum up/down time
F | Uncertainty (Upper/Lower) is estimated as +/- 25 %.
G | Assumed no improvement for regulatory capability.
H | Calculated based on the parameters: Capacity factor incl. outages, Forced outage and Planned outage.
I | Assumed same uncertainty as for CCGT.
J | Assumed same percentage for uncertainty as CCGT.
K | Lower uncertainty for 2030 and 2050 are calculated based on available information for capacity factor incl. outages.
L | Assumed gradual improvement to international standard in 2050.
M | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
N | Estimation based on international data for the capability of the machine. An average of the operational data in Colombia [6] shows that minimum up time is 4,65 hours and minimum down time is 1,34 hours (for programmed stops, for non-programmed stops the time for down time ranges between 0 and 2 hours).
O | Cost uncertainties in the short term indicate the spread of current projects under operation and in development known to the authors. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the general technology improvement potential.
References (from column K):
1 | Danish Energy Agency, Technology Catalogue for Generation of Electricity and District Heating, 2024
2 | UPME, 2024, “Registro de Proyectos de Generación” database
3 | Danish Energy Agency, Ea Energy Analyses, 2024, Technology Data for the Indonesian Power Sector
4 | Danish Energy Agency, Ea Energy Analyses, 2023, Viet Nam Technology Catalogue for Power Generation
5 | Data from Sinergox - calculation provided by Emergente
6 | Data from Paratec - Projects from 2010 on (8 units for SCGT)
7 | Ramirez-Tovar, A., Moreno-Chuquen, R., & Moreno-Quintero, R. (2022). Land-use in the Electric Colombian System: Hidden Impacts and Risks of Large-scale Renewable Projects. International Journal of Energy Economics and Policy, 12(2), 127–134. https://doi.org/10.32479/ijeep.11631
8 | Bilateral meetings with stakeholders
9 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
10 | Institute of Hydrology, Meteorology and Environmental Studies (IDEAM), Informe del inventario nacional de gases efecto invernadero 1990-2018 y carbono negro 2010-2018 de Colombia - Tercer Informe Bienal de Actualización de Cambio Climático de Colombia
11 | Danish Energy Agency, Ea Energy Analyses, 2022, Technology Data for the Indian Power Sector

## 12. MSW
| Technology | Incineration Power Plant - Municipal Solid Waste
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 15.4 | 15.95 | 16.225 | 10 | 50 | 10 | 50 | M | 5.6
| Generating capacity for total power plant (MWe) | 15.4 | 15.95 | 16.225 | 10 | 50 | 10 | 50 | M | 5.6
| Electricity efficiency, net (%), name plate | 29.47% | 30.53% | 31.05% | 28% | 31.5% | 29.5% | 32.5% |  | 2,3,6
| Electricity efficiency, net (%), annual average | 28% | 29% | 29.5% | 26.6% | 29.92% | 28.02% | 30.87% |  | 2,3,6
| Forced outage (%) | 1% | 1% | 1% | 1% | 1% | 1% | 1% |  | 1
| Planned outage (weeks per year) | 2.85 | 2.58 | 2.11 | 2.43 | 3.28 | 1.58 | 2.64 |  | 1
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1,4,6
| Construction time (years) | 3 | 2.5 | 2.5 | 2.5 | 3.5 | 2 | 3 |  | 4,6
| Space requirement (1000 m2/MWe) | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 | I | 4.6
Additional data for non thermal plants
| Capacity factor (%), theoretical | 96.18% | 96.18% | 96.18% |  |  |  |  | H | 5.6
| Capacity factor (%), incl. outages | 90% | 90.49% | 91.36% |  |  |  |  | L | 5.6
Ramping configurations
| Ramping (% per minute) | 10% | 10% | 10% | 7.5% | 12.5% | 7.5% | 12.5% | C | 1
| Minimum load (% of full load) | 20% | 20% | 20% | 15% | 25% | 15% | 25% | C | 1
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.375 | 0.625 | 0.375 | 0.625 | C | 1
| Cold start-up time (hours) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | C | 1
Environment
| SO2 (degree of desulphuring, %) | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 98.96% | 99.9% |  | 1
| NOX (g per GJ fuel) | 60 | 40 | 10 | 10 | 60 | 10 | 60 |  | 1
| CH4 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 1
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | 3 | 1 | 3 |  | 1
Financial data
| Nominal investment ( million $/MWe) | 5.3755 | 5.3113 | 5.1028 | 3.0717 | 7.6792 | 2.9159 | 7.2897 | A,B,D,E,J,K,N | 5,6
| - of which equipment (%) | 59% | 53.97% | 50% | 44.25% | 73.75% | 37.5% | 62.5% | A,B,C,E | 1,2,3
| - of which installation (%) | 41% | 46.03% | 50% | 30.75% | 51.25% | 37.5% | 62.5% | A,B,F | 1,2,3
| Fixed O&M ($/MWe/year) | 432000 | 427000 | 410000 | 324000 | 540000 | 307500 | 512500 | A,B,C,G | 6
| Variable O&M ($/MWh) | 36.536 | 36.0998 | 34.6829 | 27.402 | 45.67 | 26.0122 | 43.3536 | A,B,C | 6
Start-up costs ($/MWe/start-up)
Technology specific data
| Waste treatment capacity (tonnes/h) | 20 | 20 | 20 |  |  |  |  | D | 4.6
| Calorific content (GJ/ton) | 11 | 11 | 11 | 10 | 12 | 10 | 12 | D | 4,5,6
Notes (from column J):
A | Based on prices from countries with similar MSW compositions
B | Assuming that cost fall 0.2% each year
C | Uncertainty (Upper/Lower) is estimated as +/- 25 %.
D | Assumed a waste treatment of 20 tonnes/hour [6] and an energy content of 11 GJ/ton [5][6].
E | Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
F | Installation includes civils works (including waste bunker) and project cost considering LOT-based tendering.
G | Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
H | 2024 estimate is calculated based on the capacity incl. outages, forced outages and planned outages. 2030 and 2050 estimates are assumed to be the same as 2024.
I | Space requirements have been calculated based on plants in North and South America.
J | Central estimate for 2024 is based on 525 USD/ton waste treated/year. Uncertainty (Upper/Lower) in 2024 is based on 300 USD/ton waste treated/year and 750 USD/ton waste treated/year. Cost uncertainty in the long term follows the relative spread of short-term uncertainty, while also expressing the general technology improvement potential.
K | The estimates shown do not take into account the local conditions and are subject to many factors, such as the price of steel. Hence, they are considered to be within a plus or minus 20% accuracy [6].
L | The increasing capacity factor incl. outages in 2030 and 2050 is calculated based on the reduction of forced and planned outages.
M | The installed capacity is based on several parameters such as the calorific content in the waste, the electricity efficiency, the amount of waste treated per hour and the capacity factor incl. outages [6]. The result has also been compared to plants with similar conditions in South America.
N | Investment costs includes: Site preparation, access, landscaping; buildings, stack; grate, boiler, air supply, ash handling, electrical and mechanical systems; turbine generator; air pollution control system; contingency.
References (from column K):
1 | Danish Energy Agency, Technology Catalogue for Generation of Electricity and District Heating, 2024
2 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
3 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
4 | Bilateral meetings with stakeholders
5 | Adriana Patricia Agudelo Montoya et al., Uniminuto, 2023, Análisis de la capacidad de generación de energía eléctrica de los RSU de Medellín y viabilidad económica de la implementación de una planta WTE de los RSU estudiados
6 | Nickolas J. Themelis et al., EEC/IDB, 2013, Guidebook for the application of waste to energy technologies in Latin America and the Caribbean

## 13.a. Nuclear PWR
| Technology | Nuclear power plant - PWR
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1000 | 1000 | 1000
| Generating capacity for total power plant (MWe) | 2000 | 2000 | 2000 |  |  |  |  | B
| Electricity efficiency, net (%), name plate | 36.53 | 38 | 42 |  |  |  |  | C | 4
| Electricity efficiency, net (%), annual average | 33.64 | 36 | 40 |  |  |  |  | C | 4
| Forced outage (%) | 2 | 2 | 2 | [5 empty] | 4
| Planned outage (weeks per year) | 9 | 8 | 6 | [5 empty] | 4
Auxiliary Power Consumption (%)
| Technical lifetime (years) | 60 | 60 | 60 | [5 empty] | 1,4
| Construction time (years) | 7.4 | 7.4 | 7.4 | 4 | 10 |  |  |  | 1,4
| Space requirement (1000 m2/MWe) | 2.6206 | 2.6206 | 2.6206 | 2.023 | 3.3663 | 2.023 | 3.3663 | D | 8,9
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 4 | 4 | 3 | 3 | 5 |  |  | A | 5,4
| Minimum load (% of full load) | 25 | 25 | 25 |  |  |  |  | A | 5
| Warm start-up time (hours) | 2 | 2 | 1 | 2 | 6 |  |  |  | 5
| Cold start-up time (hours) | 30 | 30 | 30 | 24 | 48 |  |  |  | 4
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Ramp Down Rate (% of Full Load/Minute)
Minimum Up time (hours)
Minimum Down time (hours)
Hot Start-up fuel consumption (Mcal/MW)
Warm Start-up fuel consumption (Mcal/MW)
Cold Start-up fuel consumption (Mcal/MW)
Environment
| PM 2.5 (mg per Nm3) | - | - | - | - | - | - | -
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOx (g per GJ fuel) | - | - | - | - | - | - | -
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 9 | 7.9 | 6.8 | 7 | 12 | 5 | 10 | E,F,G,H | 2,3,7,10
| - of which equipment | 3 | 2.6333 | 2.2667 |  |  |  |  | F
| - of which installation | 6 | 5.2667 | 4.5333 |  |  |  |  | F
| Fixed O&M ($/MWe/year) | 127000 | 120000 | 113000 | 20000 | 180000 | 20000 | 180000 |  | 2,3
| Variable O&M ($/MWh) | 2.4 | 2.3 | 2.2 | 1.8 | 3 | 1.65 | 2.75 | I | 2,3,7
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes:
A | Ramping and minimum load are constrained by the core stability'. Minimum requirements are usually set by the regulation.
B | A two-unit configuration is typical in nuclear power plants, but more units can be combined.
C | Generation IV reactors are expected to achieve efficiencies well above 45 %. In the future, nuclear reactors are likely' to run often at partial load - thus the gap between nameplate and net efficiency
D | Nuclear power plants have a very' high energy' density' in terms of area required. The values represented here are for the area needed for the plants. However, there can be a higher requirement based on government regulation and environmental concerns F High variation in cost seen between US. EU costs and China. India costs. Moreover, this also depends on technology'. Here the chosen values are estimated based on a mix of values available along with employing the learning curve approach used for financial parameters.
E | Decommissioning costs usually are the 15% of the total investment cost, is not included in the investment cost
F | The CAPEX breakdown is composed by 33% share of direct cost (i.e., Equipment, Labour, Construction, Materials and Building), 37% of Indirect cost (i.e., Design services, Construction and Supervision and project management, Commissioning and start-up costs), 17% of Financial costs, 10% of Owner's cost.
G | The development of the overnight cost is based on NREL ATB 2023
H | CAPEX shall reflect a potential first of a kind plant according to [2]. As limited data is available for these, specific cost information of recently and currently developed plants in various markets is consulted, spanning France, UK, China and the UAE [11], excluding data for Russia, South Korea and USA not being representative due to maturity of market, political and macroeconomic situations.
I | Uncertainty (Upper/Lower) is estimated as +/- 25 %.
References:
1 | N. IEA, “Projected cost of generating electricity 2020 Edition,” Int. ENERGY AGENCY Nucl. ENERGY AGENCY Organ. Econ. CO-OPERATION Dev., no. January, p. 112, 2020, [Online]. Available: https://ncdc.gov.ng/themes/common/docs/protocols/111_1579986179.pdf
2 | O. NEA, “Unlocking Reductions in the Construction Costs of Nuclear: A Practical Guide for Stakeholders,” 2020. doi: 10.1787/9789264303119-en.
3 | “Economics of Nuclear Power(Updated August 2022).” https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power.aspx#CapitalCosts
4 | NEA, “Technical and Economic Aspects of Load Following with Nuclear Power Plants,” 2023.Nuclear Power Reactors in the World ¦ IAEA
5 | NEA, “Technical and Economic Aspects of Load Following with Nuclear Power Plants,” 2011. https://www.oecd-nea.org/upload/docs/application/pdf/2021-12/technical_and_economic_aspects_of_load_following_with_nuclear_power_plants.pdf
6 | https://www.voanews.com/a/pakistan-signs-4-8-billion-nuclear-power-plant-deal-with-china/7144967.html
7 | NREL, 2023, Annual Technology Baseline
8 | US Dept. of Energy, Office of Nuclear Energy. The ultimate fast facts guide to Nuclear Energy.
9 | STRATA. The Footprint of Energy: Land use of US Electricity Production 2017
10 | Lazard LCOE+ April 2023
11 | Rystad Energy, Global Nuclear Energy Review 2024

## 13.b. Nuclear SMR
| Technology | Nuclear power plant - SMR (Land based Water-cooled)
|  | 2024 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 80 | 80 | 80 | [5 empty] | 2,3,4
| Generating capacity for total power plant (MWe) | 300 | 300 | 300 | 10 | 300 | 10 | 300 |  | 2,3,4
| Electricity efficiency, net (%), name plate | 27 | 27 | 30 |  |  |  |  | B | 2
| Electricity efficiency, net (%), annual average | 27 | 27 | 30 |  |  |  |  | B | 2,1,4
| Forced outage (%) | 3 | 3 | 3 | [5 empty] | 2,1
| Planned outage (weeks per year) | 6.5 | 6 | 5 | 3 | 7 |  |  |  | 2
| Technical lifetime (years) | 30 | 40 | 50 | [5 empty] | 2,3
| Construction time (years) | 9 | 8 | 4 | 8 | 12 | 4 | 12 | G | 2,3, 13
| Space requirement (1000 m2/MWe) | 0.63823 | 0.63823 | 0.63823 | 0.041791 | 1.6 | 0.041791 | 1.6 | C | 11
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 1.2 | 1.2 | 1.2 |  |  |  |  | A | 2.5
| Minimum load (% of full load) | 25 | 25 | 20 |  |  |  |  | A | 1,2,5
| Warm start-up time (hours) | 1.5 | 1.5 | 1.5 | [5 empty] | 2.5
| Cold start-up time (hours) | 24 | 24 | 24
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Ramp Down Rate (% of Full Load/Minute)
Minimum Up time (hours)
Minimum Down time (hours)
Hot Start-up fuel consumption (Mcal/MW)
Warm Start-up fuel consumption (Mcal/MW)
Cold Start-up fuel consumption (Mcal/MW)
Environment
| PM 2.5 (mg per Nm3) | - | - | - | - | - | - | -
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOx (g per GJ fuel) | - | - | - | - | - | - | -
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O(g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | - | 9.6 | 7.3 | 5.6 | 20 | 5 | 10 | D,E | 8,10,12,13
| - of which equipment | - | 3.2 | 2.4333 | [5 empty] | 2,3,6
| - of which installation | - | 6.4 | 4.8667 | [5 empty] | 2,3,6
| Fixed O&M ($/MWe/year) | - | 110000 | 102000 | [5 empty] | 2,3,6
| Variable O&M ($/MWh) | - | 2.2 | 2.1 |  |  |  |  | F | 2,3,6
| Start-up costs ($/MWe/start-up) | - | 0 | 0 | 0 | 0 | 0 | 0
Notes:
A | Ramping and minimum load are constrained by the core stability'. Minimum requirements are usually set by the regulation.
B | Generation IV reactors are expected to achieve efficiencies well above 45 %. In the future, nuclear reactors are likely' to run often at partial load - thus the gap between nameplate and net efficiency
C | Nuclear power plants have a ' high energy' density' in terms of area required. The values represented here are for the area needed for the plants. However, there can be a higher requirement based on government regulation and environmental concerns F High variation in cost seen between US. EU costs and China. India costs. Moreover, this also depends on technology'. Here the chosen values are estimated based on a mix of values available along with employing the learning curve approach used for financial parameters.
D | Decommissioning costs usually are the 15% of the total investment cost
E | The CAPEX breakdown is composed by 33 % share of direct cost (i.e., Equipment, Labour, Construction, Materials and Building), 37 % of Indirect cost (i.e., Design services, Construction and Supervision and project management, Commissioning and start-up costs), 17 % of Financial costs, 10 % of Owner's cost.
F | The main characteristic are taken from CAREM-25
G | +109 mdr: China, however, managed to connect its first SMR, one of two 100 MW HTR-PM reactors, to the grid on 20 December 2021.Construction only began in 2012, and by then the time estimate for construction had increased to '50 months'. In reality, the first unit took almost 109 months from first concrete to mains connection, more than twice as long as expected
References:
1 | WNA Word Nuclear Association, economics of Nuclear Power (Updated August 2022) - https://www.world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power.aspx#ECSArticleLink1
2 | IAEA Nuclear Energy Series No. Nr-T-1.18 Technology Roadmap for small Modular Reactor Deployment, 2021- https://www-pub.iaea.org/MTCD/Publications/PDF/PUB1944_web.pdf
3 | M. A. Rahmanta, A. W. Harto, A. Agung, and M. K. Ridwan, “Nuclear Power Plant to Support Indonesia’s Net Zero Emissions: A Case Study of Small Modular Reactor Technology Selection Using Technology Readiness Level and Levelized Cost of Electricity Comparing Method,” Energies, vol. 16, no. 9, p. 3752, Apr. 2023
4 | Goswami GG, Rahman U, Chowdhury M. Estimating the economic cost of setting up a nuclear power plant at Rooppur in Bangladesh. Environ Sci Pollut Res Int. 2022 May;29(23):35073-35095. doi: 10.1007/s11356-021-18129-3. Epub 2022 Jan 19. PMID: 35044606; PMCID: PMC8767363.
5 | IAEA, “Technology Roadmap for Small Modular Reactor Deployment, IAEA Nuclear Energy Series No. NR-T-1.18,” 2021, [Online]. Available: https://www-pub.iaea.org/MTCD/Publications/PDF/PUB1944_web.pdf
6 | IEA, Nuclear Power in a Clean Energy System (2019) https://iea.blob.core.windows.net/assets/ad5a93ce-3a7f-461d-a441-8a05b7601887/Nuclear_Power_in_a_Clean_Energy_System.pdf
7 | IAEA, “Advances in Small Modular Reactor Technology Developments A Supplement to: IAEA Advanced Reactors Information System (ARIS) 2022 Edition,” 2022, [Online]. Available: https://aris.iaea.org/Publications/SMR_booklet_2022.pdf - SMR_booklet_2022.pdf (iaea.org)
8 | NREL, 2023, Annual Technology Baseline
9 | IAEA, “Advances in Small Modular Reactor Technology Developments”, 2020
10 | S. Boarin, M. Mancini, M. Ricotti, G. Locatelli, Economics and financing of small modular reactors (SMRs).
11 | Giorgio Locatelli, Benito Mignacca, Small Modular Nuclear Reactors
12 | B. Mignacca, G. Locatelli, “Economics and finance of Small Modular Reactors: A systematic review and research agenda”, Renewable and Sustainable Energy Reviews (2020), (https://doi.org/10.1016/j.rser.2019.109519)
13 | Eye-popping new cost estimates released for NuScale small modular reactor, IEEFA, January 2023 https://ieefa.org/resources/eye-popping-new-cost-estimates-released-nuscale-small-modular-reactor

## 14.a. Utility-scale Lithium-ion
| Technology | Batteries - Lithium-ion (utility-scale)
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Energy storage capacity for one unit (MWh) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | A, B
| Input capacity for one unit (MW) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A, B
| Output capacity for one unit (MW) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A, B
| Discharge time (hours) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | A, B
| Round-trip efficiency (%) AC | 90 | 92 | 92 |  |  |  |  | C | 1
| Round-trip efficiency (%) DC | 95 | 96 | 96 |  |  |  |  | C | 1
| Self-discharge rate (%/day) | 0.1 | 0.1 | 0.1 | [5 empty] | 2
| Forced outage (%) | 0.38 | 0.35 | 0.25 |  |  |  |  | M
| Planned outage (weeks per year) | 0.2 | 0.1 | 0.1 |  |  |  |  | L
| Technical lifetime (cycles) | 7500 | 10000 | 15000 |  |  |  |  | M | 3
| Technical lifetime (years) | 15 | 20 | 25 |  |  |  |  | D | 3
| Construction time (years) | 0.2 | 0.2 | 0.2
| Energy density (Wh/kg) | 150 | 200 | 300
Ramping configurations
| Response time from idle to full-rated discharge (ms) | 50 | 50 | 50 | [5 empty] | 4
| Response time from full-rated charge to discharge (sec) | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | O | 7
Financial data
| Total investment (MUSD/MWh) | 0.47127 | 0.28476 | 0.20358 | 0.3505 | 0.53575 | 0.19032 | 0.21715 | G | 1,5,6,10
| - energy component (MUSD/MWh) | 0.347 | 0.19504 | 0.13172 | 0.26 | 0.378 | 0.12163 | 0.14213 | P | 1,5,6,9,11
| - power component (MUSD/MW) | 0.329 | 0.23753 | 0.19025 | 0.242 | 0.351 | 0.18186 | 0.19861 | C, P | 1,5,6,9,11
| - other project costs (MUSD/MWh) | 0.042017 | 0.030335 | 0.024297 | 0.03 | 0.07 | 0.023226 | 0.025365 | N, P | 5,6,9
| Fixed O&M (USD/MW/year) | 15000 | 10829.6213 | 8673.9936 | 5000 | 50000 | 8291.6676 | 9055.2583 | O | 6,9,10
| Variable O&M (USD/MWh) | 2 | 1.4439 | 1.1565 | 2 | 2.6 | 1.1056 | 1.2074 | I | 7,10
Technology specific data
| Energy storage expansion cost (MUSD/MWh) | 0.38902 | 0.22538 | 0.15602 | 0.29 | 0.448 | 0.14485 | 0.1675 | F
| Output capacity expansion cost (MUSD/MW) | 0.329 | 0.23753 | 0.19025 | 0.242 | 0.351 | 0.18186 | 0.19861 | F
| Total investment (MUSD/MW) | 1.8851 | 1.139 | 0.81432 | 1.402 | 2.143 | 0.76128 | 0.8686
Notes:
A | A 4-hour battery has been picked as a reference, as there is more data available for this power-to-energy ratio in the references listed.
B | Power and energy output can be scaled linearly by utilizing many modules (up to 250 MW has been demonstrated, https://www.pv-magazine-australia.com/2023/08/10/battery-capacity-overtakes-pumped-hydro-in-nem/). Output capacity expansion can be done reprograming the management unit without any new battery module. For Utility batteries the ratio between energy storage and capacity is in general between 1 and 10 (C-rate between 1/10 and 1) only rarely the ration will be below 1.
C | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore, the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 122 [3]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4 % lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80 % and 90 % [21,22].
D | Samsung SDI 2016 whitepaper on ESS solutions provide 15-year lifetime for current modules operating at C =1/2 to C=3. Steady improvement in battery lifetime due to better materials and battery management expected. Number of cycles can be a more meaningful lifetime indicator.
E | The discharge time is the number of hours the battery can discharge at rated output capacity. It equals the Energy/Power ratio corrected for the discharge efficiency.
F | Since multi-MWh LIB systems are scalar, the energy and output capacity expansion costs are here estimated to be equal to the energy and "other cost" for energy storage expansion, and power components for output capacity expansion cost, with the other equipment and cost remaining constant respectively
G | Power conversion cost is strongly dependent on scalability and application.
H | Cost per MWh of energy discharged from the battery
I | It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
J | Cycle life specified as the number of cycles at 1C/1C to 80 % state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15-year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90 % DOD) based on chemistry [3]. Thus, for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam.
K | Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore, other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards.
L | The response time is obtained from simulated response time experiments with hardware in the loop.
M | A learning rate of 17 % is assumed for the energy components, and 10 % for power component and other costs, according to IEA and BNEF
Examples of other services with different ratios between energy storage and power output (C-rate)
The aim with this technology catalogue is to provide a brief insight into the technical aspects, current status, and forecasted price level of the LIB BESS technology. In relation to this, and to help the reader obtaining realistic prices indications, we provide two simple installation cost calculation examples below. One for frequency regulation in 2020 and one for energy integration in 2030. The examples are based on the data in the Data sheet. For simplicity neater O&M expenses nor interest rates are included in the calculations.
Energy integration in 2024: 1/2 C-rate, 1MW power output, 2MWh energy storage
| Total investment (MUSD/MWh) | 0.55352 | [5 empty] | 1 | MW
| - energy component (MUSD/MWh) | 0.347 | [5 empty] | 2 | MWh
| - power component (MUSD/MW) | 0.329
| - other project costs (MUSD/MWh) | 0.042017
Capex: 2 x (0.35+0.04)MUSD/MWh + 1 x 0.33MUSD/MW = 1.107 MUSD
Energy integration in 2024: 1/6 C-rate, 1MW power output, 6MWh energy storage
| Total investment (MUSD/MWh) | 0.44385 | [5 empty] | 1 | MW
| - energy component (MUSD/MWh) | 0.347 | [5 empty] | 6 | MWh
| - power component (MUSD/MW) | 0.329
| - other project costs (MUSD/MWh) | 0.042017
Capex: 6 x (0.35+0.04)MUSD/MWh + 1 x 0.33MUSD/MW = 2.663 MUSD
References:
1 | IEA, Battery and Secure Energy Transitions, part of World Energy Outlook 2023, April 2024
2 | Fan Xiayue, "Battery technologies for grid-level large-scale electrical energy storage", Transactions of Tianjin University, Springer, 2020.
3 | Environmental end energy study institute, Energy storage factsheet, https://www.eesi.org/papers/view/energy-storage-2019.
4 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127.
5 | Bloomberg New Energy Finance. Energy Storage System Cost Survey, 2023.
6 | NREL, 2023, Annual Technology Baseline
7 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596.
8 | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015).
9 | Danish Energy Agency, Technology Catalogue for Energy Storage, 2024
10 | Lazard, Lazard's Levelized Cost of Storage (2023)
11 | The-Future-of-Energy-Storage-MIT-2022

## 14.b. Small-scale Lithium-ion
| Technology | Batteries - Lithium-ion (small-scale)
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Energy storage capacity for one unit (MWh) | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | A, B
| Input capacity for one unit (MW) | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | A, B
| Output capacity for one unit (MW) | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | A, B
| Discharge time (hours) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | A, B
| Round-trip efficiency (%) AC | 90 | 92 | 92 |  |  |  |  | C | 1
| Round-trip efficiency (%) DC | 95 | 96 | 96 |  |  |  |  | C | 1
| Self-discharge rate (%/day) | 0.1 | 0.1 | 0.1 | [5 empty] | 2
| Forced outage (%) | 0.38 | 0.35 | 0.25 |  |  |  |  | M
| Planned outage (weeks per year) | [7 empty] | L
| Technical lifetime (cycles) | 7500 | 10000 | 15000 |  |  |  |  | M | 3
| Technical lifetime (years) | 15 | 20 | 25 |  |  |  |  | D | 3
| Construction time (years) | 0.2 | 0.2 | 0.2
| Energy density (Wh/kg) | 150 | 200 | 300
Ramping configurations
| Response time from idle to full-rated discharge (ms) | 50 | 50 | 50 | [5 empty] | 4
| Response time from full-rated charge to discharge (sec) | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | O | 7
Financial data
| Total investment (MUSD/MWh) | 1.3282 | 0.80256 | 0.57377 | 0.98784 | 1.5099 | 0.53639 | 0.61201 | G | 1,5,6,10
| - energy component (MUSD/MWh) | 0.97798 | 0.5497 | 0.37124 | 0.73278 | 1.0653 | 0.34279 | 0.40058 | P, Q | 1,5,6,9,11
| - power component (MUSD/MW) | 0.92725 | 0.66945 | 0.5362 | 0.68205 | 0.98925 | 0.51256 | 0.55976 | H, P, Q | 1,5,6,9,11
| - other project costs (MUSD/MWh) | 0.11842 | 0.085496 | 0.068478 | 0.084551 | 0.19729 | 0.06546 | 0.071488 | N, P, Q | 5,6,9
| Fixed O&M (USD/MW/year) | 42275.744 | 30522.0197 | 24446.6355 | 14091.9147 | 140919.1466 | 23369.0943 | 25521.1855 | O, Q | 6,9,10
| Variable O&M (USD/MWh) | 5.6368 | 4.0696 | 3.2596 | 5.6368 | 7.3278 | 3.1159 | 3.4028 | I, Q | 7,10
Technology specific data
| Energy storage expansion cost (MUSD/MWh) | 1.0964 | 0.6352 | 0.43972 | 0.81733 | 1.2626 | 0.40825 | 0.47207 | F
| Output capacity expansion cost (MUSD/MW) | 0.92725 | 0.66945 | 0.5362 | 0.68205 | 0.98925 | 0.51256 | 0.55976 | F
| Total investment (MUSD/MW) | 5.3128 | 3.2102 | 2.2951 | 3.9514 | 6.0398 | 2.1456 | 2.448
Notes:
A | A 4-hour battery has been picked as a reference, as there is more data available for this power-to-energy ratio in the references listed.
B | Power and energy output can be scaled linearly by utilizing many modules. Output capacity expansion can be done reprogramming the management unit without any new battery module. For smaller scale batteries the ratio between energy storage and capacity is in general between 1 and 10 with a tendency towards higher numbers (C-rate between 1/10 and 1); only rarely the ration will be below 1.
C | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore, the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 122 [3]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4 % lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80 % and 90 % [21,22].
D | Samsung SDI 2016 whitepaper on ESS solutions provide 15-year lifetime for current modules operating at C =1/2 to C=3. Steady improvement in battery lifetime due to better materials and battery management expected. Number of cycles can be a more meaningful lifetime indicator.
E | The discharge time is the number of hours the battery can discharge at rated output capacity. It equals the Energy/Power ratio corrected for the discharge efficiency.
F | Since multi-MWh LIB systems are scalar, the energy and output capacity expansion costs are here estimated to be equal to the energy and "other cost" for energy storage expansion, and power components for output capacity expansion cost, with the other equipment and cost remaining constant respectively
G | Power conversion cost is strongly dependent on scalability and application.
H | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore, the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 122 [3]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4 % lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80 % and 90 %
I | Cost per MWh of energy discharged from the battery
J | It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
K | Cycle life specified as the number of cycles at 1C/1C to 80 % state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15-year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90 % DOD) based on chemistry [3]. Thus, for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam.
L | Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore, other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards.
M | The response time is obtained from simulated response time experiments with hardware in the loop.
N | A learning rate of 17 % is assumed for the energy components, and 10 % for power component and other costs, according to IEA and BNEF
O | A proportionality factor α of 0.85 is suggested to convert the presented cost from the utility-scale datasheet to small-scale, in accordance with economy of scale found in literature
References:
1 | IEA, Battery and Secure Energy Transitions, part of World Energy Outlook 2023, April 2024
2 | Fan Xiayue, "Battery technologies for grid-level large-scale electrical energy storage", Transactions of Tianjin University, Springer, 2020.
3 | Environmental end energy study institute, Energy storage factsheet, https://www.eesi.org/papers/view/energy-storage-2019.
4 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127.
5 | Bloomberg New Energy Finance. Energy Storage System Cost Survey, 2023.
6 | NREL, 2023, Annual Technology Baseline
7 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596.
8 | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015).
9 | Danish Energy Agency, Technology Catalogue for Energy Storage, 2024
10 | Lazard, Lazard's Levelized Cost of Storage (2023)
11 | The-Future-of-Energy-Storage-MIT-2022

## 15. Hydro pumped storage
| Technology | Hydro pumped storage - natural reservoirs
|  | 2024 | 2030 | 2050 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 250 | 250 | 250 | 100 | 500 | 100 | 500 | A | 5
| Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 100 | 4000 | 100 | 4000 |  | 5
| Electricity efficiency, net (%), name plate | 80 | 80 | 80 | 75 | 82 | 75 | 82 |  | 1, 7, 8
| Electricity efficiency, net (%), annual average | 80 | 80 | 80 | 75 | 82 | 75 | 82 |  | 1, 7, 8
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 8
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 8
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 1
| Construction time (years) | 5 | 5 | 5 | 4 | 6 | 4 | 6 | F,G | 1
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 15 | 45 | 15 | 45 | F,G | 1
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 10 | 100 | 100 | 100 |  | 8, 9
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0.3 | 0.3 |  | 9
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0.3 | 0.3 |  | 9
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.2 | 1.1979 | 1.1918 | 1.0006 | 1.3491 | 0.99373 | 1.3399 | B,E,H | 1,2
| - of which equipment | 0.36 | 0.35936 | 0.35753 | 0.30018 | 0.40474 | 0.29812 | 0.40196 | B,E,I | 1,2,3
| - of which installation | 0.84 | 0.8385 | 0.83423 | 0.70043 | 0.9444 | 0.69561 | 0.93791 | B,E.I | 1,2,3
| Fixed O&M ($/MWe/year) | 24000 | 24000 | 23800 | 15000 | 33700 | 14900 | 33500 | C,E | 1,4
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Size of reservoir (MWh) | 10000 | 10000 | 10000 | 3000 | 20000 | 3000 | 20000 | D | 1,5,6
| Load/unload time (hours) | 10 | 10 | 10 | 4 | 12 | 4 | 12 | D | 1,5,6
Notes (from column J):
A | Size per turbine.
B | Numbers are very site sensitive to geographical characteristics. There will be a limited improvement by learning curve development, but best, i.e. cheap locations will be utilized first. The investment largely depends on civil work.
C | O&M assumed to be between 1.5% and 2.5%/year in line with [1] with NREL with the central value to be at 2%.
D | Size of the total plant, not per unit.
E | Cost are projected with a learning rate approach assuming a 1% learning rate for based on IEA's assumptions in their Global Energy and Climate Model, including capacity projections of the IEA's World Energy Outlook 2023, with Announced Pledges for the central values and Stated Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
F | Uncertainty (Upper/Lower) is estimated as +/- 50%.
G | Space requirements for new sites is highly uncertain given the geographical dependency. Stakeholder input has resulted in the range that is presented here.
H | Cost uncertainties in the short and long term indicate the spread of cost based on the examined cases. Cost are highly uncertain given the geographical characteristics.
I | Assuming ca. 30% share of cost amounting equipment and 70% amounting installation for large-scale RoR based on stakeholder input.
References (from column K):
1 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
2 | Danish Energy Agency, Ea Energy Analyses, Viet Nam Technology Catalogue for Power Generation, 2023
3 | IRENA, 2012, "Renewable Energy Technologies: Cost Analysis Series - Hydropower"
4 | NREL, 2023, Annual Technology Baseline
5 | Connolly, 2009, "A Review of Energy Storage Technologies - For the integration of fluctuating renewable energy"
6 | PLN 2020, Environmental and Social Management Plan (ESMP): Upper Cisokan Pumped Storage Hydropower Project 1040 MW
7 | Lazard, Lazard's Levelized Cost of Storage (2023)
8 | U.S. Department of Energy, 2015, “Hydropower Market Report”
9 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition"