## 01 Coal CHP
OPDATERET: Se dataark udgivet nov 2017

## 01 Wood Pellets
Removed March 2018, updated datasheet for large CHP Woop Pellets will be publiched in the workbook for the updated technologies before end of March 2018

## 01 Natural Gas CHP
Removed March 2018, updated datasheet for large gas CC CHP can be found in the workbook for the technologies updated August 2016 and later

## 03 Coal to biomass
OPDATERET: Se dataark udgivet aug 2016

## 04 Gas Turbine - Large
OPDATERET: Se dataark udgivet aug 2016

## 04 Gas Turbine - Medium
OPDATERET: Se dataark udgivet aug 2016

## 04 Gas Turbine - Mini
OPDATERET: Se dataark udgivet aug 2016

## 04 Gas Turbine - Micro
OPDATERET: Se dataark udgivet aug 2016

## 05 Gas Turbine - Steam Extract.
OPDATERET: Se dataark udgivet aug 2016

## 05 Gas Turbine - Back-pressure
OPDATERET: Se dataark udgivet aug 2016

## 06 Gas Engines
OPDATERET: Se dataark udgivet aug 2016

## 07 CO2 Capture and Storage
07 CO2 Capture and Storage
| Technology | CO2 capture (post-combustion), pulverized coal power plant
|  | 2010 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 500 - 740 |  |  |  |  | 1+2+3+4
| Capture efficiency (%) | 90 | 90 | 90 | 90 | A | 1
| Generation efficiency decrease (%-points) | 8-10% | 8-10% | 8-10% | 8-10% | B | 1+2+3
Financial data
Capture, post-combustion
| Nominal investment (M€/MW) | 2.3-4.3 | 3.07 | 3.00 | 2.86 | C | 1+2+3+4;2;2;2
| Fixed O&M (€/MW/year) | 72000-87000 | 72000-87000 | 72000-87000 | 72000-87000 | D | 1+2
| Variable O&M (€/MWh) | 3.4-4.1 | 3.4-4.1 | 3.4-4.1 | 3.4-4.1 | D | 1+2
References:
1 | "The Costs of CO2 Capture, Transport and Storage", Zero Emissions Platform (ZEP), July 2011
2 | "UK Electricity Generation Costs Update", Mott MacDonald, June 2010.
3 | "Energy Technology Perspectives", IEA 2010
4 | "ProjectCosts of generating Electricity", IEA & NEA, 2010
Notes:
A | The non-captured CO2 is released into the atmosphere.
B | Some of the electricity consumption may be regained as useful heat. The displayed efficiency decreases do most probably take the usage of heat into account.
C | The nominal investment is per net generating capacity, i.e. after deducting the power consumed for CO2 capture. If you compare two power plants, with CCS (this element) and without CCS (element 01), and with the same net power generating capacity, the difference in nominal investment (e.g. 3.07-2.03 = 1.04 M€/MW in 2020) is the value of the capture equipment. If CO2 capture is added on to an existing power plant, the loss in generating capacity shall be taken into account.
D | The O&M costs are per net generating capacity and net generation, i.e. after deducting the power consumer for CO2 capture.

## 08 Waste-to-Energy CHP Plant
08 Waste-to-Energy CHP Plant
| Technology | Waste to energy CHP plant
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Waste treatment capacity (tonnes/hr) | 25 - 35 |  |  |  | A
| Total efficiency (%) gross | 101 | 100 | 100 | 100 | B+C | 4
| Total efficiency (%) net | 98 | 97 | 97 | 97 | B+C | 4
| Electricity efficiency (%) gross | 28 | 30 | 30 | 30 | C | 4
| Electricity efficiency (%) net | 24 | 26 | 26 | 26 | C | 4
| Time for varm start-up (hours) | 12 | 12 | 12 |  |  | 1
| Forced outage (%) | 1 | 1 | 1 |  |  | 1
| Planned outage (weeks per year) | 3 | 3 | 3 |  |  | 1
| Technical lifetime (years) | 20 | 20 | 20 |  |  | 1
| Construction time (years) | 3 | 3 | 3 |  |  | 1
Environment
| SO2 (degree of desulphurisation, %) | 98.2 | 98.362 | 98.362 |  |  | 1
| NOX (g per GJ fuel) | 124 | 30 | 30 | 30 | C+F | 2;3;3;3
| CH4 (g per GJ fuel) | 0.59 | 0.59 | 0.59 | 0.59 |  | 2;4;4;4
| N2O (g per GJ fuel) | 1.2 | 1.2 | 1.2 | 1.2 |  | 2;4;4;4
Financial data
| Specific investment (M€ per tonnes/hr) | 4.7-6.8 | 4.7-6.8 | 4.7-6.8 | 4.7-6.8 | C+D+E+G | 4
| Specific investment (M€/MW) | 7 - 10 | 7 - 10 | 7 - 10 | 7 - 10 | C+E+G | 4
| Total O&M (€/tonne) | 53 | 53 | 53 | 53 | H | 6;4;4;4
Regulation ability
| Minimum load (% of full load) | 75 | 75 | 75 |  |  | 1
References:
1 | Rambøll Danmark, 2004
2 | National Environmental Research Institute, Denmark, 2009 (data from 2007).
3 | "En opdateret analyse af Danmarks muligheder for at reducere emissionerne af NOx" (Updated analysis of Denmark's options to reduce NOx emissions; in Danish), Danish Environmental Protection Agency, 2009.
4 | Danish Energy Agency and Energinet.dk, 2011.
5 | Affald Danmark (association of waste management companies), 2009.
6 | "BEATE. Benchmarking the waste management sector 2011" (in Danish), report delivered by waste management and industrial associations to the Danish Environment Protection Agency, 2011.
Notes:
A | tph = tonnes per hour (incineration capacity).
B | With flue gas condensation and without the use of cooling towers to dismiss surplus heat during the summer. In Denmark, the actual annual efficiency is around 93%.
C | From 2020 application of the SCR-process (selective catalytic reduction) is assumed for NOx reduction (not a legal requirement in Denmark). This implies additional investment and O&M costs, energy use for heating the flue gas and electricity loss due to increased pressure loss. The electricity efficiency is typically reduced by about 1%, while the total efficiency is reduced by about 2.5%. These impacts are included in the forecasted values for those parameters.
D | Since electricity generation is only a secondary objective of waste incineration, it may make more sense to relate the total investment to the incineration capacity, e.g. in tonnes per hour (tph), rather than the electricity generation capacity.
E | Total costs are included, including the ones relating to waste treatment and heat production.
F | Measured data on 8 plants in 2008 revealed Nox emissions between 80 and 180 g/GJ (ref. 5).
G | Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying by a factor 1.0478.
H | The quoted figure is the average total O&M for plants established in Denmark since 1999. The analysis revealed an economy-of-scale (between 50,000 and 250,000 tonnes/year): O&M (€/tonne) = 100 - 0.00025*V, where V is annually treated waste volume, in tonnes per year (ref. 6).

## 09 Woodchips Medium
09 Biomass CHP, Steam Turbine - Woodchips Medium
| Technology | Medium steam turbine, woodchips
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 10 - 50
| Electricity efficiency (%) net | 29 | 30 | 31 |  |  | 2
| Heat efficiency (%) net; without flue gas condensation | 64 |  |  |  |  | 2
| Heat efficiency (%) net; with flue gas condensation | 77 |  |  |  |  | 2
| Availability (%) | 90 | 90 | 90 |  |  | 1
| Technical lifetime (years) | 30 | 30 | 30 |  |  | 1
| Construction time (years) | 4.5 | 4.5 | 4.5 |  |  | 1
Environment
| SO2 (g per GJ fuel) | 1.9 | 1.9 | 1.9 | 1.9 |  | 3;2;2;2
| NOX (g per GJ fuel) | 81 | 81 | 81 | 81 |  | 3;2;2;2
| Unburned hydrocarbon, UHC (g per GJ fuel) | 6.1 | 6.1 | 6.1 | 6.1 |  | 3;2;2;2
| N2O (g per GJ fuel) | 0.8 | 0.8 | 0.8 | 0.8 |  | 3;2;2;2
Financial data
| Specific investment (M€/MW) | 4 | 4 | 4 | 4 |  | 4;2;2;2
| Fixed O&M (€/MW/year) | 29000 | 29000 | 29000 | 29000 | B | 1;2;2;2
| Variable O&M (€/MWh) | 3.9 | 3.9 | 3.9 | 3.9 | B | 1;2;2;2
Regulation ability
| Regulation speed (MW per min.) | 4 | 4 | 4 |  |  | 1
| Minimum load (% of full load) | 20 | 20 | 20 |  |  | 1
References:
1 | Energi E2, October 2004
2 | Danish Energy Agency and Energinet.dk, 2011., BWE 2013
3 | "Emisions map for combined heat and power production 2007", National Environmental Research Institute, Denmark, 2010.
4 | Update 2013 Ea Energianalyse: Assumed same financial data as 09 Biomass CHP, Steam Turbine - Straw Medium
Notes:
A | The Cb values have been calculated from the electricity efficiencies in condensation mode, the Cv values and a total efficiency (electricity plus heat with fluegas condensation) in full back-pressure mode of 103 %. Cf. Annex 1.
B | Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306

## 09 Woodchips Small
09 Biomass CHP, Steam Turbine - Woodchips Small
| Technology | Small steam turbine, back-pressure, woodchips
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 0.6 - 4.3
| Total efficiency (%) net | 103 | 103 | 103 |  | A | 1
| Electricity efficiency (%) net - 100% load | 25 | 25 | 25 |  |  | 1
| Time for varm start-up (hours) | 3 |  |  |  |  | 3
| Cb (50oC/100oC) | 0.3 | 0.3 | 0.3
| Availability (%) | 90 -92 | 90 -92 | 90 -92 |  |  | 1
| Technical lifetime (years) | 20 | 20 | 20 |  |  | 4
| Construction time (years) | 2-3 | 2-3 | 2-3 |  |  | 4
Environment
| SO2 (g per GJ fuel) | 1.9 | 1.9 | 1.9 | 1.9 |  | 7;6;6;6
| NOX (g per GJ fuel) | 81 | 81 | 81 | 81 |  | 7;6;6;6
| Unburned hydrocarbon, UHC (g per GJ fuel) | 6.1 | 6.1 | 6.1 | 6.1 |  | 7;6;6;6
| N2O (g per GJ fuel) | 0.8 | 0.8 | 0.8 | 0.8 |  | 7;6;6;6
Financial data
| Nominal investment (M€/MW) | 5-7 | 5-7 | 5-7 | 5-7 |  | 8
| Total O&M (% of investment per year) | 3 - 4 | 3 - 4 | 3 - 4 | 3 - 4 |  | 1
| Total O&M (€/MW/year) | 150000
References:
1 | Danish Energy Agency, 2010
2 | Elforsk: ”El från nya anläggningar”, Stockholm, 2000.
3 | Danish Technology Institute: "Udvikling af computerbaseret værktøj, energyPRO, til simulering og optimering af driftsstrategi for biobrændselsfyrede kraftvarmeværker", 2001
4 | Elkraft System, October 2003 and September 2004
5 | "Potential contribution of bioenergy to the World's future energy demand", International Energy Agency, 2007.
6 | Danish Energy Agency and Energinet.dk, 2011.
7 | "Emisions map for combined heat and power production 2007", National Environmental Research Institute, Denmark, 2010.
8 | Ea Energi Analyse 2013 update incl. industry interviews
Notes:
A | Flue-gas condensation

## 09 Straw Medium
09 Biomass CHP, Steam Turbine - Straw Medium
| Technology | Medium steam turbine, straw
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 10 - 50
| Electricity efficiency (%) net - 100% load | 29 |  |  |  |  | 1
| Heat efficiency (%) net; without flue gas condensation | 64 |  |  |  |  | 1
| Heat efficiency (%) net; with flue gas condensation | 72 |  |  |  |  | 1
| Technical lifetime (years) | 25 |  |  |  |  | 3
Construction time (years)
Environment
| SO2 (g per GJ fuel) | 49 | 49 | 49 | 49 |  | 4;3;3;3
| NOX (g per GJ fuel) | 125 | 125 | 125 | 125 |  | 4;3;3;3
| Unburned hydrocarbon, UHC (g per GJ fuel) | 0.94 | 0.94 | 0.94 | 0.94 |  | 4;3;3;3
| N2O (g per GJ fuel) | 1.1 | 1.1 | 1.1 | 1.1 |  | 4;3;3;3
Financial data
| Specific investment (M€/MW) | 4 |  |  |  | A | 1
| Fixed O&M (€/MW/year) | 40000 |  |  |  | B | 3
| Variable O&M (€/MWh) | 6.4 |  |  |  | B | 3
References:
1 | Presentation on Fyn Power Plant, Unit 8 (36 MW el with flue-gas condensation) by Vattenfall , October 2006
2 | "Potential contribution of bioenergy to the World's future energy demand", International Energy Agency, 2007.
3 | Danish Energy Agency and Energinet.dk, 2011.
4 | "Emisions map for combined heat and power production 2007", National Environmental Research Institute, Denmark, 2010.
Notes:
A | 40 % has been added to the 2006 cost, due to the general price jump for steam power plants during and after the global financial crisis 2007-2009.
B | O&M data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053

## 09 Straw Small
09 Biomass CHP, Steam Turbine - Straw Small
| Technology | Small steam turbine, back-pressure, straw
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 8 - 10
| Total efficiency (%) net | 90 | 90 | 90 |  |  | 1
| Electricity efficiency (%) net | 29 - 30 | 29 - 30 | 29 - 30 |  |  | 1
| Time for varm start-up (hours) | 2 |  |  |  |  | 3
| Availability (%) | 91 | 91 | 91 |  |  | 2
Planned outage (weeks per year)
| Technical lifetime (years) | 20 | 20 | 20 |  |  | 4
| Construction time (years) | 2 - 3 | 2 - 3 | 2 - 3 |  |  | 2
Environment
| SO2 (g per GJ fuel) | 49 | 49 | 49 | 49 |  | 6;5;5;5
| NOX (g per GJ fuel) | 125 | 125 | 125 | 125 |  | 6;5;5;5
| Unburned hydrocarbon, UHC (g per GJ fuel) | 0.94 | 0.94 | 0.94 | 0.94 |  | 6;5;5;5
| N2O (g per GJ fuel) | 1.1 | 1.1 | 1.1 | 1.1 |  | 6;5;5;5
Financial data
| Nominal investment (M€/MW) | 5-7 | 5-7 | 5-7 | 5-7 | A;B | 7
| Total O&M (% of investment per year) | 4 | 4 | 4 | 4 |  | 1
Total O&M (€/MW/year)
References:
1 | Danish Energy Agency, 2004
2 | Elsam's and Elkraft's update of the Danish Energy Authority's 'Teknologidata for el- og varmeproduktionsanlæg', 1997
3 | Danish Technology Institute: "Udvikling af computerbaseret værktøj, energyPRO, til simulering og optimering af driftsstrategi for biobrændselsfyrede kraftvarmeværker", 2001
4 | Elkraft System, October 2003
5 | Danish Energy Agency and Energinet.dk, 2011.
6 | "Emisions map for combined heat and power production 2007", National Environmental Research Institute, Denmark, 2010.
7 | Ea Energi Analyse 2013 update. Own evaluation based on industry interviews
Notes:
A | A cost reduction of 2 % per year cost is assumed
B | 40 % has been added to the 2004 cost, due to the general price jump for steam power plants during and after the global financial crisis 2007-2009.

## 10 Stirling
10 Stirling Engines, Gasified Biomass
| Technology | Stirling engine, fired by gasified biomass
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity electric, (kW) | 37 | 40 |  |  |  | 1
| Generating capacity, heat, (kJ/s) | 120 | 120 |  |  |  | 1
| Electrical efficiency (%) | 20 | 22 |  |  | A | 1
| Time for wam-up (hours) | 1 | 1 |  |  |  | 1
| Forces outage (%) | 4 | 3 |  |  |  | 1
| Planned outage (weeks per year) | 3 | 2 |  |  |  | 1
| Technical lifetime (years) | 15 | 15 |  |  |  | 1
| Construction time (years) | 0.4 | 0.3 |  |  | B | 1
Environment
| SO2 (degree of desulphuring, %) | 0 | 0 |  |  |  | 1
| NOx (ppm) | 130 | 100 |  |  |  | 1
| CH4 (ppm) | 0 | 0 |  |  |  | 1
| N20 (ppm) | 0 | 0 |  |  |  | 1
Financial data
| Specific investment costs (M€/MW) | 5 | 3.8 |  |  | C+E | 1
| Fixed O&M (€/MW/year) | 32000 | 32000 |  |  | D+E | 1
| Variable O&M (€/MWh) | 26 | 21 |  |  | D+E | 1
References:
1 | Stirling DK, December 2009
Notes:
A | The efficiency of the gasifier is 97%, while the total efficiency for the whole system is 90% (2020).
B | The plants may be delivered as pre-assembled container solutions reducing construction times on site to a couple of weeks.
C | Complete plant, including gasifier, combustion chambers, engines, control system, piping, and instrumentation.
D | O&M for the Stirling engine itself is (2010) around 16 €/MWh, while the remianing O&M costs are for biomass feeding, gasification, heat exchangers etc.
E | Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053