## 40 Large Heat Pumps - amb.temp.
OPDATERET: Se dataark udgivet aug 2016

## 40 Large Heat Pumps - 35 dgs
OPDATERET: Se dataark udgivet aug 2016

## 40 Abs. Heat Pumps - Flue Gas
OPDATERET: Se dataark udgivet aug 2016

## 40 Abs. Heat Pumps - Geothermal
OPDATERET: Se dataark udgivet aug 2016

## 41 Electric Boilers
Updated sheet publiched June 2017

## 42 Waste-to-Energy - DHP
Updated sheet publiched March 2018

## 43 Wood Chips - DHP
Updated sheet publiched March 2018

## 43 Wood Pellets - DHP
Updated sheet publiched March 2018

## 43 Straw - DHP
Updated sheet publiched March 2018

## 44 Natural Gas- DHP
44 District Heating Boiler, Gas Fired
| Technology | District heating boiler, gas fired
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one plant (MJ/s) | 0.5 - 10 | 0.5 - 10 | 0.5 - 10 |  |  | 2
| Total efficiency (%) net | 97 - 105 | 97 - 105 | 97 - 105 |  | A | 5
| Availability (%) | 98 - 99 | 98 - 99 | 98 - 99 |  |  | 2
| Technical lifetime (years) | 30 - 40 | 30 - 40 | 30 - 40 |  |  | 2
| Construction time (years) | 0.5 - 1 | 0.5 - 1 | 0.5 - 1 |  |  | 1
Environment (Fuel: natural gas)
| NOX (g per GJ fuel) | 10 - 13 | 9 - 12 | 8 - 11 | 7 - 10 |  | 5
| CH4 (g per GJ fuel) | < 3 | < 3 | < 3 | < 3 |  | 5
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 |  | 4;3;3;3
Financial data
| Nominal investment (M€ per MJ/s) | 0.07 - 0.13 | 0.07 - 0.13 | 0.07 - 0.13 |  |  | 2
| Total O&M (€ per MJ/s per year) | 1200 - 6200 | 1200 - 6200 | 1200 - 6200 |  |  | 1
References:
1 | Elsams og Elkrafts opdatering af Energistyrelsens 'Teknologidata for el- og varmeproduktionsanlæg', 1997
2 | Danish District Heating Association, 2012
3 | Danish Energy Agency, 2009
4 | National Environmental Research Institute, Denmark, 2009 (data from 2007).
5 | Danish Gas Technology Centre, 2012
Notes:
A | The highest efficiencies are due to flue gas condensation.

## 45 Geothermal - Abs.HP 70 dgs
45 Geothermal District Heating - Absorption Heat Pump - 70 C
| Technology | Geothermal heat-only plant with steam-driven absorption heat pump, Denmark
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Temperature of geothermal heat (degrees C) | approx. 70 |  |  |  |  | 1
| Heat from geothermal source (%) | 100 | 100 | 100 |  |  | 1
| Steam demand, heat pump (%) | 76 | 76 | 76 |  |  | 1
| Heat generation capacity (%) | 176 | 176 | 176 |  |  | 1
| District heat forward temperature, winter (C) | 80 | 80 | 80 |  |  | 1
| Electricity consumption for pumps etc. (%) | 8 | 8 | 8 |  | A | 1
| Technical lifetime (years) | 25 | 25 | 25 |  |  | 1
| Construction time (years) | 4-5 | 4-5 | 4-5 |  |  | 1
Financial data
| Specific investment (M€ per MJ/s geothermal heat) | 1.7622 | 1.7622 | 1.7622 |  |  | 1
| O&M excl. electricity consumption (€/year per MJ/s geothermal heat) | 47000 | 47000 | 47000 |  |  | 1
References:
1 | Dansk Fjernvarmes Geotermiselskab, 2011
Notes:
A | This is the total electricity demand for submerged pumps and reinjection pumps. Earlier versions of this document showed consumption of the same level for each of the pumps. This was an error.

## 45 Geothermal - Abs.HP 50 dgs
45 Geothermal District Heating - Absorption Heat Pump - 50 C
| Technology | Geothermal heat-only plant with steam-driven absorption heat pump, Denmark
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Temperature of geothermal heat (degrees C) | approx. 50 |  |  |  |  | 1
| Heat from geothermal source (%) | 100 | 100 | 100 |  |  | 1
| Steam demand, heat pump (%) | 107.6923 | 107.6923 | 107.6923 |  |  | 1
| Heat generation capacity (%) | 207.6923 | 207.6923 | 207.6923 |  |  | 1
| District heat forward temperature, winter (C) | 80 | 80 | 80 |  |  | 1
| Electricity consumption for pumps etc. (%) | 4.6923 | 4.6923 | 4.6923 |  |  | 1
| Technical lifetime (years) | 25 | 25 | 25 |  |  | 1
| Construction time (years) | 4-5 | 4-5 | 4-5 |  |  | 1
Financial data
| Specific investment (M€ per MJ/s geothermal heat) | 1.9987 | 1.9987 | 1.9987 |  |  | 1
| O&M excl. electricity consumption (€/year per MJ/s geothermal heat) | 49000 | 49000 | 49000 |  |  | 1
References:
1 | Dansk Fjernvarmes Geotermiselskab, 2011
Notes:
A | Usually geothermal reservoirs at a lower temperature will be shallower than reservoirs with higher temperatures. This will lead to higher permeability lower pressure drops in the reservoir and therefore lower electricity consumption for pumps.

## 45 Geothermal - Electric HP
45 Geothermal District Heating - Electric Heat Pump
| Technology | Geothermal heat-only plant with electric heat pump, Denmark
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Temperature of geothermal heat (degrees C) | approx. 70 |  |  |  |  | 1
| Heat from geothermal source (%) | 100 | 100 | 100 |  |  | 1
| Electricity demand, heat pump (%) | 17.3228 | 17.3228 | 17.3228 |  |  | 1
| Heat generation capacity (%) | 117.1654 | 117.1654 | 117.1654 |  |  | 1
| District heat forward temperature, winter (C) | 85 | 85 | 85 |  |  | 1
| Electricity consumption for pumps etc. (%) | 8.0315 | 8.0315 | 8.0315 |  | A | 1
| Technical lifetime (years) | 25 | 25 | 25 |  |  | 1
| Construction time (years) | 4-5 | 4-5 | 4-5 |  |  | 1
Financial data
| Specific investment (M€ per MJ/s geothermal heat) | 1.6 | 1.6 | 1.6 |  |  | 2
| O&M excl. electricity consumption (€/year per MJ/s geothermal heat) | 37000 | 34000 | 34000 |  |  | 2
References:
1 | Dansk Fjernvarmes Geotermiselskab, 2011
2 | Estimated by Danish Energy Agency and Energinet.dk, 2011.
Notes:
A | Earlier versions of this document showed an electricity consumption of approx. 9 %. However, the exact consumption will always depend on the local situation. For similar conditions (temperature, depth and permeability) the electricity consumption for pumps will be comparable, irrespective of whether a steam driven or electricity driven heat pump is used for heat extraction. The estimated consumption has thus been adjusted to match the consumption of the steam driven system described further above.

## 46 Solar District Heating
46 Solar District Heating
| Technology | Solar district heating
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Collector output, MWh/m2/year | 0.5 |  | 0.5 |  | A | 1
| Technical lifetime, years | 30 | 30 | 30 |  |  | 3
Financial data
| Cost of solar collectors, pipes included, €/m2 | 227.1267 |  | 156.1496 |  |  | 1.2
Investment cost of total solar system, € pr MWh/year
| Without heat store | 425.4367 | 385.8315 | 306.621 |  | C | 1
| With diurnal heat store included | 461.2091 | 421.6039 | 342.3935 |  | C | 1
| O&M costs, €/MWh | 0.56782 | 0.56782 | 0.56782 |  | B+C | 2
References:
1 | Danish Energy Agency, 2010.
2 | "Fact sheet on solar heat" (in Danish), www.solvarmecenter.dk; 2010.
3 | "Life expectancy of solar collectors in solar district heating systems", Department of Civil Engineering, Technical University of Denmark, 2009.
Notes:
A | The yield is very site-specific, depending much on the temperatures of the district heating network. The quoted yield is for a typical Danish installation without a heat pump to decrease the inlet temperature.
B | Electricity consumption included; maintenance is around 0,55 €/MWh
C | Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053