## 50 Pumped Hydro Storage
50 Pumped Hydro Storage
| Technology | Pumped hydro storage
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 10-1000 | 10-1000 | 10-1000 | 10-1000 | A | 2
| Total efficiency (%) net | 70 - 80 | 70 - 80 | 70 - 80 | 70 - 80 | A | 1
| Technical lifetime (years) | 50 | 50 | 50 | 50 | A | 1
| Construction time (years) | 2-3 | 2-3 | 2-3 | 2-3 | A
Financial data
| Investment, pump part (M€/MW) | 0.6 | 0.6 | 0.6 | 0.6 | B;C;A | 1&2
| Investment, total, greenfield plant (M€/MW) | < 4 | < 4 | < 4 | < 4 | D;A | 4
| Fixed O&M (€/MW/year) - 1-2% of investment | 6-12,000 | 6-12,000 | 6-12,000 | 6-12,000 | B;A | 3
| Variable O&M (€/MWh) | Depends on power price
References:
1 | BKK, presentation on Nygard Pumpekraftverk
2 | Tonstad Pumpekraftverk, Sira-Kvina kraftselskap, 2002
3 | BKK and Sira-Kvina
4 | “Energy technology perspectives 2008”, International Energy Agency, 2008.
Notes:
A | No significant technology advance or cost decrease is expected, since hydropower and water pumping are established technologies.
B | Based on the September 2004 exchange rate of 1NOK = 0,12€
C | Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306
D | Cf. paragraph 'Additional remarks' above.

## 51 Compr. Air Energy Storage
51 Compressed Air Energy Storage
| Technology | Compressed Air Energy Storage (CAES)
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 100 - 350
| Electricity efficiency (%) net | 60 | 71 | 71 | 71 | A | 1
| Time for warm start-up (hours) | 0 | 0 | 0 | 0 |  | 2
| Starting reliability (%) | 99 | 99 | 99 | 99 |  | 3
| Availability (%) | 95 | 95 | 95 | 95 |  | 3
| Technical lifetime (years) | 30 | 30 | 30 | 30 |  | 2
| Construction time (years) | 3 | 3 | 3 | 3 |  | 2
Environment
| NOX (kg per GJ fuel) | < 0,006 | < 0,002 | < 0,002 | < 0,002 | B | 4
| CH4 (kg per GJ fuel) | 0.0015 | 0.0015 | 0.0015 | 0.0015 |  | 4
| N2O (kg per GJ fuel) | 0.0022 |  |  |  |  | 4
Financial data
| Investment storage, € per kWh storage volume | 240 | 246.1237 | 246.1237 | 246.1237 | C+D | 5
| Investment converter, € per kW output capacity | 2000 | 1970 | 1970 | 1970 | C+D | 5
| Fixed O&M (€/MW/year) | < 14,000 | < 14,000 | < 14,000 | < 14,000 | C+E | 3
| Variable O&M (€/MW/year) | - | - |  |  | F
Regulation ability
| Fast reserve (MW per 15 minutes) | 100% | 100% | 100% | 100% |  | 1
References:
1 | “30 years compressed air energy storage plant Huntorf – Experiences and outlook”, presentation by P. Radgen, E.ON Energie, at the “Third International Renewable Energy Storage Conference (IRES 2008)”, Berlin, November 2008.
2 | KBB GmbH (a Schlumberger company),
3 | EPRI-DOE Handbook of Energy Storage for Transmission and Distribution Applications, EPRI, 2003
4 | It is estimated that emissions will be similar to Gasturbine single cycle so data is copied from technology sheet no. 04.
5 | “Economical and technical evaluation of energy storage systems”, presentation by J. Oberschmidt & M. Klobasa, Fraunhofer Institut, at the “Third International Renewable Energy Storage Conference (IRES 2008)”, Berlin, November 2008.
Notes:
A | The 2010 efficiency data is for the two plants in operation. Efficiency improvements are based on a concrete case study.
B | NOx emission today 25 ppm, 2010-15 < 9 ppm and 2020-30 < 1 ppm.
C | No significant cost decrease is expected, since all equipments are established technologies.
D | The two investment components shall be added, cf. paragraph 1.3 in the introductive chapter.
E | Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306
F | Variable O&M costs depend mainly on power and gas consumption and the specific fuel costs.

## 52 Batteries NaS
52 Batteries - NaS
| Technology | Sodium Sulphur (NaS)
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Storage capacity (MWh) | 100 | 100 | 100 |  |  | 2
| Generating capacity for one battery (MW) | 10 | 10 | 10 |  |  | 2
| Charge-discharge ratio | 2:1 |  |  |  | A | 2
Cell efficiency (%)
| System efficiency (%), AC to AC, net | 85% |  |  |  |  | 3
| Lifetime in full charge-discharge cycles | 2500 |  |  |  |  | 2
| Technical lifetime (years) | 15 | 15 | 15 |  |  | 5
| Construction time (months) | 6-8 |  |  |  |  | 1
Financial data
| Specific investment, storage capacity (k€/MWh) | 210-940 | 136 | 136 |  | D | 7;4;4
| or specific investment, output capacity (M€/MW) | 1.8-2.6 | 1.7 | 1.7 |  | D | 4+5+6;4,4
| Fixed O&M (€/MW/year) | 51000 | 51000 | 51000 |  | D | 4
| - do - | 7100 |  |  |  | D | 5
| Variable O&M (€/MWh) | 5.2865 | 5.2865 | 5.2865 |  | B+D | 4
| - do - | 15.6279 |  |  |  | C+D | 5
References:
1 | Commercial Deployment of the NaS Battery in Japan, by Hyogo Takami, Tokyo Electric Power Company and Toyoo Takayama, NGK Insulators, Ltd.
2 | Electric energy storage solution group, R&D center, engineering R&D division, Tokyo electric power company (e-mail)
3 | NAS battery energy storage system for power quality support in Malaysia, Siam, Hyogo Takami, (TEPCO)
4 | EPRI-DOE Handbook of Energy Storage for Transmission and Distribution Applications, EPRI, 2003.
5 | "Economic valuation of energy storage for utility.scale applæications", Dan Mears, Technology Insigths (Canada) at Workshop on Electricity Storage, Toronto, June 18 2008.
6 | Information from NGK Insulators Ltd. (www.ngk.co.jp/english), Japan, to Danish Energy Authority, September 2008
7 | Electricity Storage Association, California, http://electricitystorage.org/tech/technologies_comparisons_capitalcost.htm
Notes:
A | Number of hours it takes to charge the battery for having one hour to discharge the battery.
B | Based on 2500 operating hours a year
C | Assuming 1000 hours/year. If the battery is used for regulation control and black start, the variable O&M is only 3 €/MWh.
D | Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053

## 52 Batteries VRB
52 Batteries - VRB
| Technology | Vanadium Redox (VRB)
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
Storage capacity (MWh)
| Generating capacity for one unit (MW) | 10 | 10 | 10 |  |  | 1
| System efficiency (%), DC to DC, net | 80 |  |  |  |  | 3
| System efficiency (%), AC to AC, net | 70 |  |  |  |  | 4
| Lifetime in full charge-discharge cycles | 13000 |  |  |  |  | 1
| Construction time (months) | 6-8 |  |  |  |  | 1
Financial data
| Investment storage, k€ per MWh storage volume | 70 | 51 | 51 | 51 | C | 4
| Investment converter, M€ per MW output capacity | 1.5 | 1.1 | 1.1 | 1.1 | C | 4
| Fixed O&M (€/MW/year) | 54000 | 54000 | 54000 |  | A | 2
| Variable O&M (€/MWh) | 2.7662 | 2.7662 | 2.7662 |  | A;B | 2
References:
1 | VRB Power Systems Incorporated, an electrochemical Energy Storage Company, Executive Summary
2 | EPRI-DOE Handbook of Energy Storage for Transmission and Distribution Applications, EPRI, 2003.
3 | “Vanadium redox flow battery”, presentation by M. Schreiber, Cellstrom, at the “Third International Renewable Energy Storage Conference (IRES 2008)”, Berlin, November 2008
4 | “Economical and technical evaluation of energy storage systems”, presentation by J. Oberschmidt & M. Klobasa, Fraunhofer Institut, at the “Third International Renewable Energy Storage Conference (IRES 2008)”, Berlin, November 2008
Notes:
A | Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306
B | Based on 2500 operating hours a year
C | A 27% cost decrease for the mature technology is expected (ref.2).

## 60 Heat Storage - Water Pits
60 Seasonal Heat Storage - Water Pits
| Technology | Seasonal heat storage in water pits
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Store volume (m3) | 60000
| Storage capacity, kWh/m3 | 60-80 |  |  |  |  | 2
| Efficiency, % | 80-95 |  |  |  | A | 3
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 |  | 3
| Technical lifetime (years) | 20 | 20 | 20 | 20 | B | 3
Financial data
| Specific investment costs (€ per m3) | 35.4962 | 35.4962 | 33.7214 | 30.1718 | C | 1;3;3;3
| Electricity consumption (MWh/year) | 39.5073 |  |  |  | D | 3
| O&M (% of investment per year) | 0.7 |  |  |  |  | 3
References:
1 | “Seasonal heat storages in district heating networks”, Ellehauge & Kildemoes and Cowi, July 2007. A project (Preheat) funded by Intelligent Energy – Europe and the Danish systems operator Energinet.dk.
2 | Dirk Mangold: “Seasonal Heat Storage. Pilot projects and experiences in Germany”. Presentation at the PREHEAT Symposium at Intersolar 2007, Freiburg, Germany, June 2007.
3 | Planenergi (Danish company; www.planenergi.dk), which in 2010 is installing a 60,000 m3 pit store in Northern Jutland.
Notes:
A | The storage loss depends on several parameters, such as store volume, insulation, whether a heat pump is part of the system etc. The stated interval covers a large store, storage temperature 85-90 C, without (80%) and with (95%) a heatpump to discharge the store.
B | The most critical part is the cover. The technical lifetime depends much on the water temperature. The lifetime of the store may be extended by reinvesting in a new cover.
C | 2010: Budget cost for a 60,000 m3 pit. The cost development assumes a 10-20% reduction from 2020 to 2050, caused by replication of pits, pipes, pumps, heat exchangers and control system. For other store volumes, please refer to paragraph 'Additional remarks' above.
D | Electricity for internal pumps etc. only. If a heat pump is used, the drive electricity shall be added.
E | Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053

## 61 Large-scale Hot Water Tanks
61 Large-scale Hot Water Tanks
| Technology | Large steel tanks for heat storage
|  | 2010 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Storage capacity, kWh/m3 | 60-80 |  |  |  |  | 1
| Efficiency, % | 95 |  |  |  | A
Environment
Financial data
| Specific investment costs (€ per m3) | 160-260 |  |  |  | B | 2
O&M
References:
1 | Dirk Mangold: “Seasonal Heat Storage. Pilot projects and experiences in Germany”. Presentation at the PREHEAT Symposium at Intersolar 2007, Freiburg, Germany, June 2007.
2 | “Heat storage technologies”. Report, June 2007, from the PREHEAT project, funded by the Intelligent Energy – Europe programme (www.preheat.org).
Notes:
A | This is an example: A 10,000 m3 store operating between 90 and 50 C, an outdoor temperature of 5 C, and a storage cycle of one week. Cf. description above under 'Additional remarks'.
B | Store volume 10,000 m3.

## 71 Underground Storage of Gas
71 Underground Storage of Gas
Cavern leaching
Plant for cavern leaching | Mill. €
Total | 9.858
Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
Mill. €
Construction and equipment | 22.11
Cushion gas for one cavern (40% of total) | 14.0828
Total cost, 100 mio Nm3 active volume | 36.1928
Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW),
withdrawal 600,000 nM3/hour (approx. 6600 MW)
Mill. €
Construction work | 2.8166
Compressors, incl. auxiliaries | 30.1372
Udtrækstog | 12.9562
Withdrawal equipment | 4.5065
Connections, transformer, regulation, and instruments | 12.6745
Total investment cost | 63.0909
A new greenfield store, equivalent to Lille Torup in Denmark, would require
one leaching plant, 5 caverns, and one process plant.
Total investment cost | 253.9129 | mill. €
Operation and maintenace, salt cavern, 400-500 million m3 working gas
Mill. € per year
Electricity | 0.7 - 1.1
Gas consumption to reheat extracted gas | 0.13
Total, incl. administration | 6.5

## 72 Hydrogen Storage
72 Hydrogen Storage
| Technology | Hydrogen storage, cavern
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Output capacity, MW | 2 |  |  |  |  | 1
| Storage volume, MWh | 10 |  |  |  |  | 1
| Overall cycle efficiency, AC-AC (%) | 35 |  |  |  | A | 1
| Technical lifetime (year) | 30 |  |  |  |  | 1
Financial data
| Investment storage, € per kWh storage volume | 11 |  |  |  | A+B+C | 1
| Investment converter, € per kW output capacity | 3000 |  |  |  | A+B+C | 1
Fixed O&M (€/MW/year)
Variable O&M (€/MWh)
References:
1 | “Economical and technical evaluation of energy storage systems”, presentation by J. Oberschmidt & M. Klobasa, Fraunhofer Institut, at the “Third International Renewable Energy Storage Conference (IRES 2008)”, Berlin, November 2008
Notes:
A | System: PEM electrolysis, storage of hydrogen at 30 bar, and a gas engine to convert back to AC.
B | The two investment components shall be added, cf. paragraph 1.3 in the introductive chapter.
C | Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053