## 1 Coal subcritical
Technology
| Technology |  | Subcritical coal power plant
|  | Currently cases | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 300 | 600 | 600 | 600 | 100 | 650 | 100 | 650 |  | 1
| Generating capacity for total power plant (MWe) | 300 | 1200 | 1200 | 1200 | 100 | 1500 | 100 | 1500 |  | 1
| Electricity efficiency, net (%), name plate | #REF! | 37.4625 | 37 | 37 | 30 | 38 | 33 | 39 |  | 1;2;3
| Electricity efficiency, net (%), annual average | #REF! | 34.935 | 35 | 36 | 29 | 37 | 32 | 38 |  | 1;2;3
| Forced outage (%) | - | 7 | 5 | 3 | 5 | 20 | 2 | 7 | A | 1
| Planned outage (weeks per year) | - | 6 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | - | 3.25 | 3.25 | 3.25 | 2 | 4 | 2 | 4 |  | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | #REF! | 1.0308 | 3.5 | 3.5 | 1 | 4 | 2 | 4 | B | 1
| Minimum load (% of full load) | #REF! | 67.1933 | 25 | 20 | 25 | 70 | 10 | 30 | A | 1
| Warm start-up time (hours) | #REF! | 5.2 | 3 | 3 | 1 | 5 | 1 | 5 | B | 1
| Cold start-up time (hours) | #REF! | 10.25 | 8 | 8 | 5 | 10 | 5 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | #REF! | 70 | 70 | 70 | 50 | 150 | 20 | 100 | A;E | 2;4
| SO2 (degree of desulphuring, %) |  | 86 | 86 | 95 | 73 | 95 | 73 | 95 | A | 2;4
| NOX (g per GJ fuel) |  | 152 | 150 | 38 | 152 | 262.5 | 38 | 262.5 | A;C | 2;4
Financial data
| Nominal investment (M$/MWe) | #REF! | 1.12 | 1.213 | 1.1754 | 0.79575 | 1.2884 | 0.79575 | 1.2884 | D;G | 1;3
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | #REF! | 39400 | 38200 | 37000 | 29600 | 49300 | 27800 | 46300 | F | 1;3
| Variable O&M ($/MWh) | #REF! | 0.7 | 0.12125 | 0.1175 | 0.090938 | 0.7 | 0.088125 | 0.14687 | F | 1;3
| Start-up costs ($/MWe/start-up) | #REF! | 300 | 110 | 110 | 50 | 300 | 50 | 200 |  | 5
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from currently regulation of coal thermal plant on environment of Viet Nam
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
Notes:
A | Assumed gradual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability from 2030 to 2050
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
D | For economy of scale a proportionality factor, a, of 0.8 is suggested.
E | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as +/- 25%.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 1 Coal supercritical
Technology
| Technology | Supercritical coal power plant
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  | 1
| Generating capacity for total power plant (MWe) | 1200 | 1200 | 1200 | 300 | 1800 | 300 | 1800 |  | 1
| Electricity efficiency, net (%), name plate | 37.6667 | 38.7967 | 39.9267 | 33 | 40 | 35 | 42 |  | 1;3;6;7
| Electricity efficiency, net (%), annual average | 36.6667 | 37.7667 | 38.8667 | 33 | 40 | 35 | 42 |  | 1;3
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 3.75 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 1 | 4 | 4 | 1 | 4 | 3 | 4 | B | 1
| Minimum load (% of full load) | 75 | 25 | 20 | 25 | 75 | 10 | 30 | A | 1
| Warm start-up time (hours) | 8 | 4 | 4 | 2 | 8.5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 10 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 70 | 70 | 70 | 50 | 150 | 20 | 100 | E | 2;4
| SO2 (degree of desulphuring, %) | 86 | 86 | 95 | 73 | 95 | 73 | 95 |  | 2;4
| NOX (g per GJ fuel) | 152 | 150 | 38 | 152 | 262.5 | 38 | 262.5 | C | 2;4
Financial data
| Nominal investment (M$/MWe) | 1.38 | 1,39 | 1.37 | 0.7 | 1.75 | 0.7 | 1.645 | D;F;G | 1;3;6;7
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 41200 | 40000 | 38700 | 30900 | 51500 | 29000 | 48400 | F | 1;3;6;7
| Variable O&M ($/MWh) | 0.12 | 0.1164 | 0.1128 | 0.09 | 0.97 | 0.0846 | 0.141 | F | 1;3
| Start-up costs ($/MWe/start-up) | 50 | 50 | 50 | 40 | 100 | 40 | 100 |  | 5
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | IEA, World Energy Outlook, 2015.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability from 2030 to 2050
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
D | For economy of scale a proportionality factor, a, of 0.8 is suggested.
E | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as +/- 25%.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 1 Coal ultra-supercrital
Technology
| Technology | Ultra-supercritical coal power plant
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
| Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
| Electricity efficiency, net (%), name plate | 42.5 | 43.775 | 45.05 | 40 | 45 | 42 | 47 |  | 1;3;6;7
| Electricity efficiency, net (%), annual average | 41.5 | 42.745 | 43.99 | 40 | 45 | 42 | 47 |  | 1;3
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 4.3333 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 5 | 5 | 5 | 4 | 5 | 4 | 5 | B | 1
| Minimum load (% of full load) | 30 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1
| Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 70 | 70 | 70 | 50 | 150 | 20 | 100 | E | 2;4
| SO2 (degree of desulphuring, %) | 86 | 86 | 95 | 73 | 95 | 73 | 95 |  | 2;4
| NOX (g per GJ fuel) | 152 | 150 | 38 | 152 | 262.5 | 38 | 262.5 | C | 2;4
Financial data
| Nominal investment (M$/MWe) | 1.51 | 1.49 | 1.48 | 0.8 | 1.906 | 0.8 | 1.7917 | D;F;G | 1;3;6;7
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 56600 | 54900 | 53200 | 42500 | 70800 | 39900 | 66500 | F | 1;3;6;7
| Variable O&M ($/MWh) | 0.11 | 0.1067 | 0.1034 | 0.0825 | 0.1375 | 0.07755 | 0.12925 | F | 1;3
| Start-up costs ($/MWe/start-up) | 50 | 50 | 50 | 40 | 100 | 40 | 100 |  | 5
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | IEA, World Energy Outlook, 2015.
Notes:
A | Assumed gradual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability from 2030 to 2050
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
D | For economy of scale a proportionality factor, a, of 0.8 is suggested.
E | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as +/- 25%.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 2 SCGT
Technology
| Technology | Simple Cycle Gas Turbine - large system
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 50 | 50 | 50 | 35 | 65 | 35 | 65 |  | 3
| Generating capacity for total power plant (MWe) | 100 | 100 | 100 | 35 | 150 | 35 | 150 |  | 3
| Electricity efficiency, net (%), name plate | 33.5 | 36 | 40 | [5 empty] | 1;2
| Electricity efficiency, net (%), annual average | 32.5 | 35 | 39 | [5 empty] | 1;2
| Forced outage (%) | 2 | 2 | 2
| Planned outage (weeks per year) | 3 | 3 | 3
| Technical lifetime (years) | 25 | 25 | 25
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.125 | 1.875 | 1.125 | 1.875 | B | 3
| Space requirement (1000 m2/MWe) | 0.02 | 0.02 | 0.02 | 0.015 | 0.025 | 0.015 | 0.025 | B | 3
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 3;8
| Minimum load (% of full load) | 20 | 30 | 15 | 30 | 50 | 10 | 40 | A | 6
| Warm start-up time (hours) | 0.25 | 0.23 | 0.2 | [5 empty] | 3
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 7
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
| NOX (g per GJ fuel) | 86.4 | 60 | 20 | 20 | 86 | 20 | 86 | A;D | 3;7
Financial data
| Nominal investment (M$/MWe) | 0.59 | 0.57 | 0.54 | 0.35 | 1.2 | 0.35 | 0.8 | F;G | 1-5
| - of which equipment (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| - of which installation (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| Fixed O&M ($/MWe/year) | 23200 | 22500 | 21800 | 17400 | 29000 | 16400 | 27300 | B | 1-5
Variable O&M ($/MWh)
| Start-up costs ($/MWe/start-up) | 24 | 24 | 24 | 18 | 30 | 18 | 30 | B | 6
References:
1 | IEA, Projected Costs of Generating Electricity, 2015.
2 | IEA, World Energy Outlook, 2015.
3 | Danish Energy Agency, 2015, "Technology Catalogue on Power and Heat Generation".
4 | Learning curve approach for the development of financial parameters.
5 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
6 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
7 | Maximum emission from Minister of Environment Regulation 21/2008
8 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
9 | Soares, 2008, "Gas Turbines: A Handbook of Air, Land and Sea Applications".
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Assumed no improvement for regulatory capability.
D | Calculated from a max of 400 mg/Nm3 to g/GJ (conversion factor 0.27 from Pollution Prevention and Abatement Handbook, 1998)
E | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
F | The investment cost of an aero-derivative gas turbine will be in the higher end than an industrial gas turbine (ref. 5) . Roughly 50% higher.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 2 CCGT
Technology
| Technology | Combined Cycle Gas Turbine
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 750 | 750 | 750 | 200 | 800 | 200 | 800 |  | 1
| Generating capacity for total power plant (MWe) | 1500 | 1500 | 1500 | 200 | 1600 | 200 | 1600 |  | 1
| Electricity efficiency, net (%), name plate | 56 | 60 | 61 | 45 | 62 | 55 | 65 |  | 1;3;5;10
| Electricity efficiency, net (%), annual average | 52 | 59 | 60 | 39 | 61 | 54 | 64
| Forced outage (%) | 5 | 5 | 5 | 3 | 10 | 3 | 10 |  | 1
| Planned outage (weeks per year) | 5 | 5 | 5 | 3 | 8 | 3 | 8 |  | 1
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 7 | 20 | 20 | 10 | 30 | 10 | 30 | C | 1;2
| Minimum load (% of full load) | 56 | 30 | 15 | 30 | 50 | 10 | 40 | A | 5
| Warm start-up time (hours) | 2 | 1 | 1 | 1 | 3 | 0.5 | 2 | A | 1;5
| Cold start-up time (hours) | 3 | 2 | 2 | 2 | 5 | 2 | 5 |  | 1;5
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
| NOX (g per GJ fuel) | 78 | 60 | 20 | 20 | 86 | 20 | 86 | A;D | 7;8
Financial data
| Nominal investment (M$/MWe) | 0.76513 | 0.69 | 0.68 | 0.55 | 0.77 | 0.55 | 0.77 | F | 1;3;10
| - of which equipment (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| - of which installation (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| Fixed O&M ($/MWe/year) | 29350 | 28500 | 27600 | 22000 | 36700 | 20700 | 34500 | B | 1;3
| Variable O&M ($/MWh) | 0.45036 | 0.1261 | 0.1222 | 0.33777 | 0.56295 | 0.09165 | 0.15275 | B | 1
| Start-up costs ($/MWe/start-up) | 69.5115 | 70 | 70 | 52.1336 | 86.8894 | 52.5 | 87.5 | B | 6
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
3 | IEA, World Energy Outlook, 2015.
4 | Learning curve approach for the development of financial parameters.
5 | Siemens, 2010, "Flexible future for combined cycle".
6 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
7 | Maximum emission from Minister of Environment Regulation 21/2008
8 | Danish Energy Agency, 2015, "Technology Catalogue on Power and Heat Generation".
9 | Soares, 2008, "Gas Turbines: A Handbook of Air, Land and Sea Applications".
10 | IEA, Projected Costs of Generating Electricity, 2015.
Notes:
A | Assumed gradual improvement to international standard in 2050.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Assumed no improvement for regulatory capability.
D | Calculated from a max of 400 mg/Nm3 to g/GJ (conversion factor 0.27 from Pollution Prevention and Abatement Handbook, 1998)
E | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
F | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 3 Small hydro
Technology
| Technology | Hydro power plant - Small system
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 30 | 30 | 30 | 1 | 30 | 1 | 30 |  | 2
| Generating capacity for total power plant (MWe) | 30 | 30 | 30 | 1 | 30 | 1 | 30 |  | 2
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 1
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 1
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 1
| Construction time (years) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 1
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | 10.5 | 17.5 | 10.5 | 17.5 | B
Additional data for non thermal plants
| Capacity factor (%), theoretical | 80 | 80 | 80 | 50 | 95 | 50 | 95 |  | 8;9
| Capacity factor (%), incl. outages | 75.8846 | 75.8846 | 75.8846 | 50 | 95 | 50 | 95 |  | 8;9
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 3
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.75 | 1.75 | 1.75 | 0.8 | 4 | 0.8 | 4 | C;D | 4;5;6;7
| - of which equipment (%) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 7
| - of which installation (%) | 70 | 70 | 70 | 50 | 80 | 50 | 80 |  | 7
| Fixed O&M ($/MWe/year) | 41900 | 39800 | 37300 | 22000 | 41900 | 22000 | 41900 |  | 4;5;7
| Variable O&M ($/MWh) | 0.5 | 0.475 | 0.445 | 0.375 | 0.625 | 0.33375 | 0.55625 | B | 1
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
Size of reservoir (MWh)
References:
1 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
2 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
5 | IEA, World Energy Outlook, 2015.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
8 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
9 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 3 Large hydro
Technology
| Technology | Hydro power plant - large system
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 150 | 150 | 150 | 30 | 2000 | 30 | 2000 |  | 1;8;10
| Generating capacity for total power plant (MWe) | 150 | 150 | 150 | 30 | 2000 | 30 | 2000 |  | 1;8;10
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 | B | 1
| Construction time (years) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Space requirement (1000 m2/MWe) | 62 | 62 | 62 | 46.5 | 77.5 | 46.5 | 77.5 | C | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 40 | 40 | 40 | 20 | 95 | 20 | 95 |  | 2;12
| Capacity factor (%), incl. outages | 35.8846 | 35.8846 | 35.8846 | 20 | 95 | 20 | 95 |  | 2;12
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 3
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.5 | 1.5 | 1.5 | 0.6 | 8 | 0.6 | 8 | D;E | 1;4;5;6;9
| - of which equipment (%) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 11
| - of which installation (%) | 70 | 70 | 70 | 50 | 80 | 50 | 80 |  | 11
| Fixed O&M ($/MWe/year) | 37700 | 35800 | 33600 | 28300 | 47100 | 25200 | 42000 | C | 1;4;5;6
| Variable O&M ($/MWh) | 0.65 | 0.6175 | 0.5785 | 0.4875 | 0.8125 | 0.43388 | 0.72313 | C | 1;5
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
Size of reservoir (MWh)
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | IEA, World Energy Outlook, 2015.
5 | Learning curve approach for the development of financial parameters.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
8 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
9 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
10 | General Electric, www.gerenewableenergy.com, Accessed: 20th July 2017
11 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
12 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Hydro power plants can have a very long lifetime is operated and mainted properbly. Hover Dam in USA is almost 100 years old.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 4 Solar PV
Technology
| Technology | Solar PV - Large scale grid connected
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWp) | 0.0002 | 0.0002 | 0.0002 |  |  |  |  | C | 5
| Generating capacity for total power plant (MWac) | 50 | 50 | 50 | 10 | 200 | 1 | 50 |  | 1
| Electricity efficiency, net (%), name plate | - | - | - | - | - | - | - | A
| Electricity efficiency, net (%), annual average | - | - | - | - | - | - | - | A
| Forced outage (%) | - | - | - | - | - | - | -
| Planned outage (weeks per year) | - | - | - | - | - | - | -
| Technical lifetime (years) | 25 | 25 | 25 | 15 | 35 | 20 | 40 |  | 1;6
| Construction time (years) | 1 | 0.5 | 0.5 | 0.5 | 1.5 | 0.25 | 1 |  | 1;9
| Space requirement (1000 m2/MWac) | 14.4 | 13.2 | 13.2 | 8.4 | 18 | 6 | 18 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 21.1187 | 21.6895 | 22.8311 | 14 | 22 | 16 | 23 |  | 1;2
| Capacity factor (%), incl. outages | 21.1187 | 21.6895 | 22.8311 | 14 | 22 | 16 | 23 |  | 1;2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | - | B
| Cold start-up time (hours) | - | - | - | - | - | - | - | B
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWac) | 1.1 | 0.84 | 0.65 | 0.7 | 2 | 0.4 | 0.8 | D;R | 1;3;4
| - of which equipment (%) | 51 | 50 | 47
| - of which installation (%) | 49 | 50 | 53
| Fixed O&M ($/MWac/year) | 11000 | 8800 | 7400 | 8300 | 13800 | 5600 | 9400 | Q | 5;6
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWac/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1900 | 1900 | 1900 |  |  |  |  | F | 7
| DC/AC sizing factor (Wp/Wac) | 1.2 | 1.2 | 1.2 |  |  |  |  | G | 9;10
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 7
| Performance ratio (%) | 0.81 | 0.84 | 0.87 |  |  |  |  | I | 5;6
| PV module conversion efficiency (%) | 19 | 23 | 26 | [5 empty] | 6
| Availability (%) | 100 | 100 | 100 | [5 empty] | 6
| Inverter lifetime (years) | 15 | 15 | 15 | [5 empty] | 6
Output
| Full load hours (kWh/kWac) | 1850 | 1900 | 2000 |  |  |  |  | J; L
| Peak power full load hours (kWh/kWp) | 1550 | 1600 | 1650 |  |  |  |  | K; L
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | IEA, World Energy Outlook, 2015.
4 | Learning curve approach for the development of financial parameters.
5 | Cirata 1 MW Solar PV O&M and Financial Perspective, Sharing Experience. PJB.
6 | Danish Technology Catalogue “Technology Data for Energy Plants, 2012, PV updated in 2015.
7 | PVGIS © Europeen Communitees 2001-2012.
8 | Learning curve based forecast of technology costs. Ea Energy Analyses, 2017
9 | Gelex Ninh Thuan PV solar photovoltaic plant located in Thuan Nam district, Ninh Thuan province with installed capacity of 50 MWp
10 | Bau Ngu lake PV plant located in Ninh Phuoc and Thuan Nam district, Ninh Thuan province with 61.8 MWp of installed capacity
Notes:
A | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
B | The production from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
C | Listed as MWe. The MWp will be around 10% higher.
D | Assumptions described in the section "Assumptions and perspectives for further development"
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. 1900 kWh/m2 corresponds to a good location at Java.
G | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is set to the same value for all years, as it is not the technical factors of the system, which determine the sizing factor. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio (PR) of a photovoltaic system is the quotient of alternating current (AC) yield and the nominal yield of the generator’s direct current (DC). ThePR factor considers losses due to low irradiance, high temperature and losses in cables and inverter. The performance ratio is lower for PV plants in Indonesia compared to Northern European locations because temperature losses are higher in Indonesia. PJB's on-going project on a location at Simeulue Island, Aceh, expects a performance ratio of 80 %.
J | The number of full load hours is calculated based on the other values in the table. The calculation formula is: Full load hours = 1046 * sizing factor * transposition factor * performance ratio
K | Also known as the specific yearly energy production (kWh/kWp) of the PV modules. This value is calculated from this formula: Peak power full load hours = 1046 * transposition factor * (1-incident angle modifier loss) * (1-PV system losses etc.) * (1-inverter loss) * (1-AC grid loss).
L | Capacity factor = Full load hours / 8760.
M | Current international market prices for utility scale PV systems have been estimated based on interviews with Danish developers and an assesment of the prices from Danish and Germany tenders for PV capacity in 2016 and the beginning of 2017. The forecasted internatinal price is based on estimated learning rates for the module and invester (20 % learning rate) and balance of plant (10 % learning rate) and a projection of the cumulated PV capacity based on the IEA's 450 ppm scenario. The share that the PV module and the invester accounts for decreases over time as the result of the higher learning rate compared to the balance of plant. Indonesian prices are assumed to be somewhat higher in the first years thereafter approaching gradually the international level.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters and land-lease. Annual O&M is based on the Danish TC.
R | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 5 Wind onshore
Technology
| Technology | Wind power - Onshore
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 3 | 4 | 5 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 30 | 80 | 100 | [5 empty] | 1
| Electricity efficiency, net (%), name plate | [7 empty] | A
Electricity efficiency, net (%), annual average
| Forced outage (%) | 2.5 | 2 | 2
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 |  | 3
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | [5 empty] | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | D
| Minimum load (% of full load) | - | - | - | - | - | - | - | D
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.6 | 1.31 | 1.11 | 1.4 | 2.0 | 1.0 | 1.5 | C | 1
| - of which equipment (%) | 65 | 65 | 65 |  |  |  |  | B | 2; 3
| - of which installation (%) | 35 | 35 | 35 |  |  |  |  | B | 2; 3
| Fixed O&M ($/MWe/year) | 40500 | 37800 | 35900 | 36500 | 44600 | 28700 | 43100 | E | 4
| Variable O&M ($/MWh) | 4.2375 | 3.8985 | 3.5595 | 3.8137 | 4.6612 | 2.8476 | 4.2714 | E | 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Rotor diameter (m) | 120 | 130 | 150 | 90 | 130 | 100 | 150 |  | 3
| Hub height (m) | 90 | 100 | 110 | 85 | 120 | 85 | 150 |  | 3
| Specific power (W/m2) | 309 | 301 | 283 | 270 | 350 | 250 | 350 |  | 3
| Avability (%) | 97 | 98 | 98 | 95 | 99 | 95 | 99 |  | 3
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | IRENA (2015). Renewable Power Generation Cost in 2014
3 | Danish Energy Agency, 2012/2016.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
4 | Danish Energy Agency, 2018.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
5 | Vestas data provided by the Sales Division for the Asian Pacific.
Notes:
A | The efficiency is defined as 100%. The improvement in technology development is captured in capacity factor, investment cost and space requirement.
B | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
C | The IEA expects approximately a doubling of the accumulated wind power capacity between 2020 and 2030 and 4-5 times more by 2050 compared to 2020. Assuming a learning of 12.5 % per annum this yields a cost reduction of approx. 13 % by 2030 and approx. 25 % by 2050.
D | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
E | The O&M costs have been set at 50 % higher than in the Danish TC (ref. 4 above).

## 5 Wind offshore
Technology
| Technology | Wind power - Offshore
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 3.5 | 10 | 12 | 1.6 | 8 | 4 | 20 |  | 1
| Generating capacity for total power plant (MWe) | 105 | 300 | 360 | 48 | 240 | 120 | 600 |  | 1
| Electricity efficiency, net (%), name plate | [7 empty] | A
| Electricity efficiency, net (%), annual average | [7 empty] | A
| Forced outage (%) | 4 | 3 | 3 | 1 | 5 | 1 | 5 |  | 1
| Planned outage (%) | 0.3 | 0.3 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1
| Technical lifetime (years) | 27 | 30 | 30 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 3 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 1
| Space requirement (1000 m2/MWe) | 185 | 185 | 185 | 168 | 204 | 168 | 204 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) including grid investment | 2,36 | 2.25 | 1.93 | 1.9549 | 2.75 | 1.56 | 2.15 | C | 1
| - of which equipment (%) | 45 | 45 | 45 | 40 | 50 | 40 | 50 | A | 1
| - of which installation (%) | 55 | 55 | 55 | 50 | 60 | 50 | 60 | A | 1
| Fixed O&M ($/MWe/year) | 50000 | 43000 | 36000 | 45000 | 53000 | 29000 | 40000 |  | 1; 2
| Variable O&M ($/MWh) | 3.729 | 3.051 | 2.486 | 3.39 | 3.842 | 1.921 | 2.712 |  | 1; 2
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Rotor diameter (m) | 120 | 210 | 240 | [5 empty] | 1
| Hub height (m) | 90 | 125 | 140 | [5 empty] | 1
| Specific power (W(m2) | 309.4682 | 353 | 332 | [5 empty] | 1
| Availability (%) | 97 | 97 | 98 | 95 | 99 | 95 | 99 |  | 1
References:
1 | Danish Energy Agency, 2018.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
2 | IEA Wind Task 26, 2015, "Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2007–2012".
Notes:
A | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
B | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
C | The costs for offshore (not near shore) from the Danish TC (ref. 1 above) has been used as a best estimate for offshore in Vietnam.

## 6 Biomass power plant (small)
Technology
| Technology | Biomass power plant (small plant)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1;5
| Generating capacity for total power plant (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1;5
| Electricity efficiency, net (%), name plate | 32 | 32 | 32 | 25 | 35 | 25 | 35 |  | 1;3;7
| Electricity efficiency, net (%), annual average | 31 | 31 | 31 | 25 | 35 | 25 | 35 |  | 1;3;7
| Forced outage (%) | 7 | 7 | 7 | 5.25 | 8.75 | 5.25 | 8.75 | A | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 4.5 | 7.5 | 4.5 | 7.5 | A | 1
| Technical lifetime (years) | 25 | 25 | 25 | 18.75 | 31.25 | 18.75 | 31.25 | A | 8;10
| Construction time (years) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | A | 10
| Space requirement (1000 m2/MWe) | 35 | 35 | 35 | 26.25 | 43.75 | 26.25 | 43.75 | A | 1;9
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | [5 empty] | 3
| Minimum load (% of full load) | 30 | 30 | 30 | [5 empty] | 3
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
| Cold start-up time (hours) | 10 | 10 | 10 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 12.5 | 12.5 | 12.5 | [5 empty] | 3
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [5 empty] | 3
| NOX (g per GJ fuel) | 125 | 125 | 125 | [5 empty] | 3
Financial data
| Nominal investment (M$/MWe) | 1.7202 | 1.5826 | 1.3762 | 1.2901 | 2.1502 | 1.0321 | 1.7202 | B | 4-8;11
| - of which equipment (%) | 65 | 65 | 65 | 50 | 85 | 50 | 85 |  | 1;2
| - of which installation (%) | 35 | 35 | 35 | 15 | 50 | 15 | 50 |  | 1;2
| Fixed O&M ($/MWe/year) | 47600 | 43800 | 38100 | 35700 | 59500 | 28600 | 47600 | A | 4;5;8;11
| Variable O&M ($/MWh) | 3.0433 | 2.7999 | 2.4347 | 2.2825 | 3.8042 | 1.826 | 3.0433 | A | 5;11
Start-up costs ($/MWe/start-up)
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | ASEAN Centre of Energy, 2016, "Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states".
3 | Danish Energy Agency and COWI, 2017, "Technology catalogue for biomass to energy".
4 | IRENA, 2015, "Renewable power generation cost in 2014"
5 | IFC and BMF, 2017, "Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | India Central Electricity Authority, 2007, "Report on the Land Requirement of Thermal Power Stations".
10 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
11 | Learning curve approach for the development of financial parameters.
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.
B | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 7 MSW incineration
Technology
| Technology | Incineration Power Plant - Municipal Solid Waste
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 21.5896 | 22.3341 | 23.0786
| Generating capacity for total power plant (MWe) | 21.5896 | 22.3341 | 23.0786
| Electricity efficiency, net (%), name plate | 29 | 30 | 31 | 28 | 32 | 30 | 33 | A | 1
| Electricity efficiency, net (%), annual average | 28 | 29 | 29 | 26 | 30 | 28 | 31 |  | 1
| Forced outage (%) | 1 | 1 | 1 | [5 empty] | 1
| Planned outage (weeks per year) | 2.9 | 2.6 | 2.1 | [5 empty] | 1
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | [5 empty] | 1
| Space requirement (1000 m2/MWe) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | 7.5 | 12.5 | 7.5 | 12.5 | C | 1
| Minimum load (% of full load) | 20 | 20 | 20 | 15 | 25 | 15 | 25 | C | 1
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.375 | 0.625 | 0.375 | 0.625 | C | 1
| Cold start-up time (hours) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | C | 1
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 8.7324 | 8.074 | 7.2309 | 6.5493 | 9.0386 | 5.4232 | 9.0386 | C | 1
| - of which equipment (%) | 5.1521 | 4.36 | 3.6154 | 3.8641 | 4.5193 | 2.7116 | 4.5193 |  | 1
| - of which installation (%) | 3.5803 | 3.714 | 3.6154 | 2.6852 | 4.5193 | 2.7116 | 4.5193 |  | 1
| Fixed O&M ($/MWe/year) | 243700 | 224800 | 193500 | 195000 | 304600 | 154800 | 241900 | C | 1
| Variable O&M ($/MWh) | 24.1437 | 23.3794 | 22.5829 | 18.1078 | 28.2286 | 16.9371 | 28.2286 | C | 1
Start-up costs ($/MWe/start-up)
Technology specific data
| Waste treatment capacity (tonnes/h) | 27.7 | 27.7 | 27.7 |  |  |  |  | B
References:
1 | Danish Technology Catalogue “Technology Data for Energy Plants, Danish Energy Agency 2107- update in progress
Notes:
A | Based on experience from the Netherlands where 30 % electric efficiency is achieve. 1 %-point efficiency subtracted to take into account higher temperature of cooling water in Indonesia (approx. +20 C).
B | The investment cost is based on waste to energy CHP plant in Denmark, according to Ref 1. A waste treatment capacity of 27,7 tonnes/h is assumed and an energy content of 10,4 GJ/ton. The specific finalcial data is adjusted to reflect that the plant in Indonesia runs in condensing mode and hence the electric capacity (MWe) is higher than for a combined heat and power, backpressure plant with the same treatment capacity.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Calculated from size, fuel efficiency and an average calory value for waste of 9.7 GJ/ton.

## 7 Landfill gas
Technology
| Technology | Landfill Gas Power Plant - Municipal Solid Waste
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
| Generating capacity for total power plant (MWe) | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
| Electricity efficiency, net (%), name plate | 35 | 35 | 35 | 25 | 37 | 25 | 37 |  | 2
| Electricity efficiency, net (%), annual average | 34 | 34 | 34 | 25 | 37 | 25 | 37 |  | 2
| Forced outage (%) | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
| Planned outage (weeks per year) | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1 | 3 | 1 | 3 |  | 3
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.5 | 2.5 | 2.5 | 2.2727 | 2.75 | 2.2727 | 2.875 | A | 3
| - of which equipment (%) | 70 | 70 | 70 | 70 | 80 | 70 | 80 |  | 5
| - of which installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 5
| Fixed O&M ($/MWe/year) | 125000 | 125000 | 125000 | 113640 | 137500 | 113636.3636 | 143750 | A | 3
Variable O&M ($/MWh)
Start-up costs ($/MWe/start-up)
References:
1 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority, Jakarta, Indonesia
2 | Renewables Academy" (RENAC) AG, 2014, "Biogas Technology and Biomass", Berlin, Germany.
3 | IEA-ETSAP and IRENA, 2015. "Biomass for Heat and Power, Technology Brief".
4 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
5 | MEMR, 2015, "Waste to Energy Guidebook", Jakarta, Indonesia.
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.

## 8 Biogas power plant (small)
Technology
| Technology | Biogas power plant
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 1 | 1 | 1 | [5 empty] | 3
| Electricity efficiency, net (%), name plate | 35 | 35 | 35 | [5 empty] | 4
| Electricity efficiency, net (%), annual average | 34 | 34 | 34 | [5 empty] | 4
| Forced outage (%) | 5 | 5 | 5 | [5 empty] | 1
| Planned outage (weeks per year) | 5 | 5 | 5 | [5 empty] | 1
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 7
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 7
| Space requirement (1000 m2/MWe) | 70 | 70 | 70 | [5 empty] | 12
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 |  | 11
| Minimum load (% of full load) | 20 | 30 | 15 | 30 | 50 | 10 | 40 |  | 10
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.78 | 2.5576 | 2.224 | 2.085 | 3.475 | 1.668 | 2.78 | A | 3;5;8;9
| - of which equipment (%) | 65 | 65 | 65 | 50 | 85 | 50 | 85
| - of which installation (%) | 35 | 35 | 35 | 15 | 50 | 15 | 50
| Fixed O&M ($/MWe/year) | 97000 | 89200 | 77600 | 72800 | 121300 | 58200 | 97000 | A | 5;7;9
| Variable O&M ($/MWh) | 0.11 | 0.1012 | 0.088 | 0.0825 | 0.1375 | 0.066 | 0.11 | A | 6;9
Start-up costs ($/MWe/start-up)
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | ASEAN Centre of Energy (2016). Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states.
3 | Winrock, 2015, "Buku Panduan Konversi POME Menjadi Biogas, Pengembangan Proyek di Indonesia", USAID – Winrock International.
4 | RENAC, 2014, "Biogas Technology and Biomass, Renewables Academy (RENAC)".
5 | IFC and BMF, 2017, Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | Learning curve approach for the development of financial parameters.
10 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
11 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
12 | Chazaro Gerbang Internasional, 2004, "Utilization of Biogas Generated from the Anaerobic Treatment of Palm Oil Mills Effluent (POME) as Indigenous Energy Source for Rural Energy Supply and Electrification - A Pre-Feasibility Study Report"
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.

## 9 Diesel power plant
Technology
| Technology | Diesel engine (using fuel oil)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 20 | 20 | 20 | [5 empty] | 1
| Generating capacity for total power plant (MWe) | 100 | 100 | 100
| Electricity efficiency, net (%), name plate | 46 | 47 | 48 | [5 empty] | 1
| Electricity efficiency, net (%), annual average | 45 | 46 | 47 | 43 | 47 | 45 | 52 |  | 1
| Forced outage (%) | 3 | 3 | 3
| Planned outage (weeks per year) | 0.8 | 1 | 1 | [5 empty] | 2
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 2
| Construction time (years) | 1 | 1 | 1 | [5 empty] | 2
| Space requirement (1000 m2/MWe) | 0.05 | 0.05 | 0.05 | [5 empty] | 2
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | -
| Capacity factor (%), incl. outages | - | - | -
Ramping configurations
| Ramping (% per minute) | 25 | 25 | 25
| Minimum load (% of full load) | 6 | 6 | 6 |  |  |  |  | A | 1
| Warm start-up time (hours) | 0.05 | 0.05 | 0.05 | [5 empty] | 1
| Cold start-up time (hours) | 0.3 | 0.3 | 0.3
Environment
| PM 2.5 (gram per Nm3) | 19.6 | 19.6 | 19.6 |  |  |  |  | B; C | 3;4
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 |  |  |  |  | C | 3;4
| SO2 (g per GJ fuel) | 224 | 224 | 224 |  |  |  |  | C | 3;4
| NOX (g per GJ fuel) | 280 | 280 | 280 |  |  |  |  | C | 3;4
Financial data
| Nominal investment (M$/MWe) | 0.8 | 0.8 | 0.776 | 0.7 | 0.9 | 0.65 | 0.85 | D | 6;7
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 8000 | 8000 | 7760 | [5 empty] | 2
| Variable O&M ($/MWh) | 6.4 | 6 | 5.8 | [5 empty] | 2
| Start-up costs ($/MWe/start-up) | - | - | -
References:
1 | Wärtsila, 2011, "White paper Combustion engine power plants", Niklas Haga, General Manager, Marketing & Business Development Power Plants
2 | Danish Energy Agency, 2016, "Technology Data for Energy Plants"
3 | Minister of Environment, Regulation 21/2008
4 | The International Council on Combustion Engines, 2008: Guide to diesel exhaust emissions control of NOx, SOx, particles, smoke and CO2
5 | http://www.bwsc.com/News---Press.aspx?ID=530&PID=2281&Action=1&NewsId=206
6 | BWSC once again to deliver highly efficient power plant in the Faroe Islands.
7 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
Notes:
A | 30 % minimum load per unit - corresponds to 6 % for total plant when consisting of 5 units
B | Total particulate matter
C | Typical diesel exhaut emission according to Ref 3 (average of interval) unless this number exceeds the maximum allowed emission according to Minister of Environment Regulation 21/2008. Both SO2 and particulates are dependant on the fuel composition.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 10 Geothermal - small
Technology
| Technology | Geothermal power plant - small system (binary or condensing)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 10 | 10 | 10 | 0.3 | 20 | 0.3 | 20 |  | 1;8
| Generating capacity for total power plant (MWe) | 20 | 20 | 20 | 5 | 30 | 5 | 30 |  | 1
| Electricity efficiency, net (%), name plate | 10 | 11 | 12 | 6 | 12 | 8 | 14 | A | 5
| Electricity efficiency, net (%), annual average | 10 | 11 | 12 | 6 | 12 | 8 | 14 | A | 5
| Forced outage (%) | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 1
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 30 | 31 | 32 | 20 | 40 | 20 | 40 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1
| Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | B | 6
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | B | 6
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | B | 6
Financial data
| Nominal investment (M$/MWe) | 4.525 | 4.1856 | 3.8236 | 3.3938 | 5.6562 | 2.8677 | 4.7795 | C;D;E | 1;2;4;8
| - of which equipment (%) | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 3
| - of which installation (%) | 40 | 40 | 40 | 30 | 50 | 30 | 50 |  | 3
| Fixed O&M ($/MWe/year) | 20000 | 18500 | 16900 | 15000 | 25000 | 12700 | 21100 | C;D | 1;4
| Variable O&M ($/MWh) | 0.37 | 0.34225 | 0.31265 | 0.2775 | 0.4625 | 0.23449 | 0.39081 | C;D | 1;4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Exploration costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
| Confirmation costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Budisulistyo & Krumdieck , 2014, "Thermodynamic and economic analysis for the pre- feasibility study of a binary geothermal power plant"
3 | IRENA, 2015, Renewable Power Generation Costs in 2014.
4 | Learning curve approach for the development of financial parameters.
5 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
6 | Yuniarto, et. al., 2015. “Geothermal Power Plant Emissions in Indonesia”.
7 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
8 | Climate Policy Initiative, 2015, Using Private Finance to Accelerate Geothermal Deployment: Sarulla Geothermal Power Plant, Indonesia.
Notes:
A | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in effciency will give a lower investment cost per MW. These smaller units are assumed to be binary units at medium source temperatures.
B | Geothermal do emit H2S. From Minister of Environment Regulation 21/2008 this shall be below 35 mg/Nm3.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Investment cost are including Exploration and Confirmation costs (see under Technology specific data).
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 10 Geothermal - large
Technology
| Technology | Geothermal power plant - large system (flash or dry)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 55 | 55 | 55 | 30 | 500 | 30 | 500 |  | 1
| Generating capacity for total power plant (MWe) | 110 | 110 | 110 | 30 | 500 | 30 | 500 |  | 1
| Electricity efficiency, net (%), name plate | 16 | 17 | 18 | 8 | 18 | 10 | 20 | A | 5
| Electricity efficiency, net (%), annual average | 15 | 16 | 17 | 8 | 18 | 10 | 20 | A | 5
| Forced outage (%) | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 1
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1
| Construction time (years) | 2 | 2 | 2 | 1,5 | 3 | 1,5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1
| Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1
Ramping configurations
| Ramping (% per minute) | 3 | 10 | 20 | [5 empty] | 8
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | C | 6
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | C | 6
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | C | 6
Financial data
| Nominal investment (M$/MWe) | 3.49 | 3.2283 | 2.949 | 2.6175 | 4.3625 | 2.2118 | 3.6863 | B;D;E | 1;2;3;4
| - of which equipment (%) | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 3
| - of which installation (%) | 40 | 40 | 40 | 30 | 50 | 30 | 50 |  | 3
| Fixed O&M ($/MWe/year) | 18000 | 16700 | 15200 | 13500 | 22500 | 11400 | 19000 | B;D | 1;4
| Variable O&M ($/MWh) | 0.25 | 0.23125 | 0.21125 | 0.1875 | 0.3125 | 0.15844 | 0.26406 | B;D | 1;4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Exploration costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
| Confirmation costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | IEA, World Energy Outlook, 2015.
3 | IRENA, 2015, Renewable Power Generation Costs in 2014.
4 | Learning curve approach for the development of financial parameters.
5 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
6 | Yuniarto, et. al., 2015. “Geothermal Power Plant Emissions in Indonesia”.
7 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
8 | Geothermal Energy Association, 2015, "Geothermal Energy Association Issue Brief: Firm and Flexible Power Services Available from Geothermal Facilities"
Notes:
A | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in effciency will give a lower investment cost per MW. These large units are assumed to be flach units at high source temperatures.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%, which is an estimate build upon cases from IRENA (ref. 3)
C | Geothermal do emit H2S. From Minister of Environment Regulation 21/2008 this shall be below 35 mg/Nm3.
D | The learning rate is assumed to impact the geothermal specific equipment and installation. The power plant units (i.e. the turbine and pump) is assumed to have very litle development. From Ref. 3 it is assumed that half of the investment cost are on the geothermal specific equipment.
E | Investment cost are including Exploration and Confirmation costs (see under Technology specific data).

## 11 Hydro pumped storage
Technology
| Technology | Hydro pumped storage
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 250 | 250 | 250 | 100 | 500 | 100 | 500 | A | 1;6
| Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 100 | 4000 | 100 | 4000 |  | 1;6
| Electricity efficiency, net (%), name plate | 80 | 80 | 80 | 75 | 82 | 75 | 82 |  | 1;3;5
| Electricity efficiency, net (%), annual average | 80 | 80 | 80 | 75 | 82 | 75 | 82 |  | 1;3;5
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 5
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 5
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 1
| Construction time (years) | 4.3 | 4.3 | 4.3 | 2.15 | 6.45 | 2.15 | 6.45 | B | 1
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 15 | 45 | 15 | 45 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 10 | 100 | 10 | 100 |  | 2;5
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 2
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 2
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 0.8575 | 0.8575 | 0.8575 | 0.6 | 6 | 0.6 | 6 | C;E | 1;3;4
| - of which equipment (%) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 7
| - of which installation (%) | 70 | 70 | 70 | 50 | 80 | 50 | 80 |  | 7
| Fixed O&M ($/MWe/year) | 8000 | 8000 | 8000 | 4000 | 30000 | 4000 | 30000 |  | 3;4;6.7
| Variable O&M ($/MWh) | 1.325 | 1.325 | 1.325 | 0.5 | 3 | 0.5 | 3 |  | 1;7
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Size of reservoir (MWh) | 10000 | 10000 | 10000 | 3000 | 20000 | 3000 | 20000 | D | 1;6
| Load/unload time (hours) | 10 | 10 | 10 | 4 | 12 | 4 | 12 | D | 1;6
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
3 | Lazard, 2016, “Lazard’s Levelised Cost of Storage – version 2.0”.
4 | MWH, 2009, Technical Analysis of Pumped Storage and Integration with Wind Power in the Pacific Northwest
5 | U.S. Department of Energy, 2015, “Hydropower Market Report”.
6 | Connolly, 2009, "A Review of Energy Storage Technologies - For the integration of fluctuating renewable energy".
7 | IRENA, 2012, "Renewable Energy Technologies: Cost Analysis Series - Hydropower".
Notes:
A | Size per turbine.
B | Uncertainty (Upper/Lower) is estimated as +/- 50%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | The size of the total power plant and not per unit (turbine).
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 12 Batteries
Technology |  |  | Lithium-ion battery
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Energy storage capacity for one unit (MWh) |  | 6 | 7 | 8 | 5 | 9 | 7 | 12 | A | 2;14
Output capacity for one unit (MW) |  | 18 | 21 | 24 | 16 | 21 | 22 | 28 | A,B | 2;14
Input capacity for one unit (MW) |  | 3 | 3.5 | 4 | 2.7 | 3.5 | 3.7 | 4.7 | A,B | 2;14
Round trip efficiency (%) AC |  | 91 | 92 | 92 | 90 | 92 | 91 | 94 | C | 3;21;22;51
Round trip efficiency (%) DC |  | 95 | 96 | 96 | 95 | 96 | 95 | 97 | C | 3;21;22;51
- Charge efficiency (%) |  | 98 | 98.5 | 98.5 | 98 | 98.5 | 98 | 99 | D | 2
- Discharge efficiency (%) |  | 97 | 97.5 | 97.5 | 97 | 98 | 97 | 98 | D | 2
Energy losses during storage (%/day) |  | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.15 | E | 18;50;52
Forced outage (%) |  | 0.38 | 0.35 | 0.25 | 0.2 | 0.5 | 0.1 | 0.3 | F | 0
Planned outage (weeks per year) |  | 0.2 | 0.1 | 0.1 | 0.1 | 0.25 | 0.05 | 0.2 | F | 0
Technical lifetime (years) |  | 20 | 25 | 30 | 15 | 25 | 20 | 45 | G | 3;5;8;14
Construction time (years) |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.1 | 0.25 | 0 | 38
Regulation ability
Response time from idle to full-rated discharge (sec) |  | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | H | 53
Response time from full-rated charge to full-rated discharge (sec) |  | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | H | 53
Financial data
Specific investment (M$ per MWh) |  | 0.48816 | 0.34126 | 0.15255 | 0.3616 | 0.62602 | 0.07458 | 0.34465 | I | 44;48
- energy component (M$/MWh) |  | 0.14916 | 0.07006 | 0.03955 | 0.0791 | 0.21357 | 0.02938 | 0.12995 | J | 44
- capacity component (M$/MW) PCS |  | 0.3051 | 0.1808 | 0.0678 | 0.2712 | 0.5763 | 0.0452 | 0.2825 | K | 54–56
- other project costs (M$/MWh) |  | 0.113 | 0.0904 | 0.0452 | 0.1017 | 0.1243 | 0.0226 | 0.1243 | L | 22;40;54
Fixed O&M (k$/MW/year) |  | 0.6102 | 0.6102 | 0.6102 | 0.5085 | 0.6102 | 0.452 | 0.6102 | M | 22
Variable O&M ($/MW/year) |  | 2.26 | 2.034 | 1.808 | 0.452 | 6.328 | 0.339 | 2.825 | N | 55
Technology specific data
Energy storage expansion cost (M$/MWh) |  | 0.26216 | 0.16046 | 0.08475 | 0.1808 | 0.29267 | 0.05198 | 0.19888 | O | 44;48
Output capacity expansion cost (M$/MW) |  | 0.3051 | 0.1808 | 0.0678 | 0.2712 | 0.5763 | 0.0452 | 0.2825 | P | 54–56
Alternative Investment cost (M$/MW) |  | 0.3729 | 0.226 | 0.0904 | 0.3164 | 0.6554 | 0.0565 | 0.3503 | Q | 41;44;48;54–56
Lifetime in total number of cycles |  | 14000 | 30000 | 50000 | 10000 | 16000 | 20000 | 70000 | R | 3–5;14
Specific power (W/kg) |  | 700 | 900 | 1200 | 600 | 900 | 1000 | 2000 | S | 2;24
Power density (kW/m3) |  | 800 | 1000 | 1400 | 750 | 900 | 1200 | 2000 | S | 2;24
Specific energy (Wh/kg) |  | 105 | 139 | 209 | 100 | 140 | 150 | 300 | S | 2;24
Energy density (kWh/m3) |  | 130 | 173 | 260 | 150 | 200 | 200 | 400 | S | 2;24
Data Sheet Notes:
A. One unit defined as a 40 feet container including LIB system and excluding power conversion system. Values for 2015-2030 are taken from Samsung SDI brochures for grid-connected LIBs from 2016 and 2018 [2,14]. This unit of 3.2MWh/9.6MW (3C) is a typical size grid scale battery. The Specific investment cost under financial data is provided for a 1MWh : 1MW (1C) battery. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
B. Power input/output are set to 0.5/3 times the energy capacity as it is the standard grid-connected LIBs designed for power purposes [2,14]. It is noted that the power capacity is strongly dependent on the battery type and chemistry.
C. The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
D. The C-rate is 0.5 during charge and up to 6 during discharge for the Samsung SDI batteries [2,14]. The presented conversion efficiencies assume average discharge C-rates in 2015-2020 around 3 and charge C-rates around 0.5.
E. Lithium-ion battery daily discharge loss. The central estimates for self-discharge of Li-ion batteries range between 0.05% and 0.20% a day in 2016 and are expected to stay flat to 2030.
F. It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
G. Current state-of-the-art NMC LIB has 20 years lifetime. The NMC lifetime is expected to reach LTO lifetime by 2020 and 30 years lifetime for grid-connected LIBs in 2040 and 2050 as photovoltaic power systems have today [3,5,8,14].
H. The response time is obtained from simulated response time experiments with hardware in the loop [53].
I. The system specific forecasts includes rack, TMS, BMS, EMS and PCS (Figure 5). The forecast is calculated as the sum of the PCS, the battery cell, and other costs. The system specific forecast is exclusive power cables to the site and entrepreneur work for installation of the containers [44,48]. The specific investment cost is the total cost of a 1MWh : 1MW (1C) battery. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
J. The battery pack cost forecast is provided in Figure 8 and the related text [44].
K. Power conversion cost is strongly dependent on scalability and application. The PCS cost is based on references [54–56] and reflects the necessity for high power performance and compliance to grid codes to provide ancillary services, bidirectional electricity flow and two-stage conversion, as well as the early stage of development and the fact that few manufacturers can guarantee turnkey systems. The ’energy component (M€/MWh)’, ‘capacity component (M€/MW) PCS’ and ‘other project costs (M€/MWh)’ does not sum up to the ‘Specific investment (M€2015 per MWh) since the units are individually forecasted, and since the C-rate was not assumed to be the same for all the forecasted years.
L. Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards. Estimates are aggregated from the literature [22,40,54].
M. Inverter replacement is expected every 10 years [22].
N. Variable O&M is assumed to be 2.1 €/MWh in 2015 with a range of 0.4 – 5.6 [55].
O. Since multi-MWh LIB systems are scalar, the energy storage expansion cost is here estimated to be equal to the energy component plus the “other costs” [44,48].
P. Since multi-MW LIB systems are scalar, the capacity expansion cost equals the capacity component cost [54–56].
Q. The alternative investment cost in M€2015/MW is specified for a 4C, 0.25 h system as for the Laurel Mountain, West Virginia, USA grid-scale LIB storage system [41]. I.e. the alternative investment cost is 25% of the energy storage expansion cost plus the PCS cost [41,44,48,54–56].
R. Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [3]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam. Cycle lives are steadily increasing over last few years as reflected in 2020/2030 numbers [4,5,14].
S. Specific power, power density, Specific energy and energy density is provided for discharge mode, starting with the values provided in the section “Typical characteristics and capacities”. A charge/discharge conversion factor of 12 can be derived from this section. The expected development depends on the successive R&D progress as indicated in the section “Research and development perspectives” [2,24].
References
[1] | Leclanche. Lithium Ion Technology and Product Description, (2018). http://www.leclanche.com/technology-products/leclanche-technology/lithium-ion-cells/
[2] | Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
[3] | L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
[4] | L. Kokam Co. Kokam Li-ion / Polymer Cell, (2017). http://kokam.com/data/Kokam_Cell_Brochure_V.4.pdf
[5] | StoraXe. StoraXe Industrial & Infrastructure Scalable battery storage system, (2018). https://www.ads-tec.de/fileadmin/download/doc/brochure/Datasheet_Energy_Industrial_EN.pdf
[6] | Fronius. Fronius Energy Package, (2018). http://www.fronius.com/en/photovoltaics/products/all-products/solutions/fronius-storage-solution/fronius-energy-package/fronius-energy-package
[7] | Fenecon. Fenecon Commercial 50-series Battery Module ¦ Battery Rack, (2018). https://www.fenecon.de/en_US/page/infocenter#fenecon-industrial
[8] | Altairnano. 24 V 60 Ah Battery Module, (2016). https://altairnano.com/products/battery-module/
[9] | S. Weintraub, Electrek. Tesla Gigafactory tour roundup and tidbits: ‘This is the coolest factory in the world’, (2016). https://electrek.co/2016/07/28/tesla-gigafactory-tour-roundup-and-tidbits-this-is-the-coolest-factory-ever/
[10] | M. Kane, InsideEVs. BMW i3 Samsung SDI 94 Ah Battery Rated For 524,000 Miles, (2018). https://insideevs.com/lets-look-at-the-specs-of-the-samsung-sdi-94-ah-battery/
[11] | Qnovo. Inside the Battery of a Nissan Leaf, (2018). https://qnovo.com/inside-the-battery-of-a-nissan-leaf/
[12] | J.M. Tarascon, M. Armand. Issues and challenges facing rechargeable lithium batteries, Nature, 414 (2001) 359. doi:10.1038/35104644
[13] | Shutterstock. Tesla 2170 battery cell stock photos, (2018). https://www.shutterstock.com/search/tesla+2170+battery+cell
[14] | Samsung, Smart Battery Systems for Energy Storage, (2016). http://www.samsungsdi.com/upload/ess_brochure/Samsung SDI brochure_EN.pdf
[15] | Inside EVs. LCChem Prismatic Cell, (2018). https://insideevs.com/wp-content/uploads/2015/12/ess_cell1.jpg
[16] | H.C. Hesse, M. Schimpe, D. Kucevic, A. Jossen. Lithium-ion battery storage for the grid - A review of stationary battery storage system design tailored for applications in modern power grids, Energies, 10 (2017) 2107. doi:10.3390/en10122107
[17] | M. Schimpe, M. Naumann, N. Truong, H.C. Hesse, S. Santhanagopalan, A. Saxon, A. Jossen. Energy efficiency evaluation of a stationary lithium-ion battery container storage system via electro-thermal modeling and detailed component analysis, Appl. Energy. 210 (2018) 211. doi:10.1016/j.apenenergy.2017.10.129
[18] | Electropaedia. Battery Performance Characteristics - How to specify and test a battery, (2018). https://www.mpoweruk.com/performance.htm
[19] | L. Kokam Co. Lithium Ion Polymer Cells - High Energy High PowerㅣKokam Battery Cells, (2018). http://kokam.com/cell/
[20] | Sempra Renewables. Auwahi Wind, (2012). http://www.semprarenewables.com/project/auwahi-wind/
[21] | A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
[22] | Lazard. Levelized Cost of Storage (2017)., https://www.lazard.com/perspective/levelized-cost-of-storage-2017/
[23] | R. Hidalgo-León et al. A survey of battery energy storage system (BESS), applications and environmental impacts in power systems, 2017 IEEE 2nd ETCM pp. 1–6. doi:10.1109/etcm.2017.8247485.
[24] | LG Chem. Change your energy. Change your life., (2018). http://www.lgchem.com/upload/file/product/LGChem_Catalog_Global_2018.pdf
[25] | Researchinterfaces. Lithium-ion batteries for large-scale grid energy storage, (2018). https://researchinterfaces.com/lithium-ion-batteries-grid-energy-storage/
[26] | U.S. EPA. Application of Life-Cycle Assessment to Nanoscale Technology: Lithium-ion Batteries for Electric Vehicles, United States Environ. Prot. Agency. (2013) 1–119. doi:10.1038/nchem.2085.
[27] | J.F. Peters, M. Baumann, B. Zimmermann, J. Braun, M. Weil. The environmental impact of Li-Ion batteries and the role of key parameters – A review, Renew. Sustain. Energy Rev. 67 (2017) 491–506. doi:10.1016/j.rser.2016.08.039
[28] | The Washington Post. The environmental impact of cobalt mining, (2018). https://www.washingtonpost.com/news/in-sight/wp/2018/02/28/the-cost-of-cobalt/?utm_term=.eebc6c00f0de
[29] | Visualcapitalist. Nickel: The Secret Driver of the Battery Revolution, (2017). http://www.visualcapitalist.com/nickel-secret-driver-battery-revolution/
[30] | Bloomberg. We’re Going to Need More Lithium, (2017). https://www.bloomberg.com/graphics/2017-lithium-battery-future/
[31] | R. Petibon, J. Xia, L. Ma, M.K.G. Bauer, K.J. Nelson, J.R. Dahn. Electrolyte System for High Voltage Li-Ion Cells, J. Electrochem. Soc. 163 (2016) A2571–A2578. doi:10.1149/2.0321613jes
[32] | A. Casimir, H. Zhang, O. Ogoke, J.C. Amine, J. Lu, G. Wu. Silicon-based anodes for lithium-ion batteries: Effectiveness of materials synthesis and electrode preparation, Nano Energy. 27 (2016) 359–376. doi:10.1016/j.nanoen.2016.07.023
[33] | M. Saulnier, A. Auclair, G. Liang, S.B. Schougaard. Manganese dissolution in lithium-ion positive electrode materials, Solid State Ionics. 294 (2016) 1–5. doi:10.1016/j.ssi.2016.06.007
[34] | E.-Y. Kim, B.-R. Lee, G. Yun, E.-S. Oh, H. Lee. Effects of binder content on manganese dissolution and electrochemical performances of spinel lithium manganese oxide cathodes for lithium ion batteries, Curr. Appl. Phys. 15 (2015) 429–434. doi:10.1016/j.cap.2015.01.029
[35] | S. Lee, E.-Y. Kim, H. Lee, E.-S. Oh. Effects of polymeric binders on electrochemical performances of spinel lithium manganese oxide cathodes in lithium ion batteries, J. Power Sources. 269 (2014) 418–423. doi:10.1016/j.jpowsour.2014.06.167
[36] | eeNews Power Management. Revolutionary solid state rechargeable aluminium-sulfur battery project starts, (2017). http://www.eenewspower.com/news/revolutionary-solid-state-rechargeable-aluminium-sulfur-battery-project-starts
[37] | Ørsted. Ørsted takes first steps into commercial energy storage, (2018). https://orsted.com/en/Media/Newsroom/News/2018/04/Orsted-takes-first-steps-into-commercial-battery-storage
[38] | Tesla. Addressing Peak Energy Demand with the Tesla Powerpack, (2016). https://www.tesla.com/da_DK/blog/addressing-peak-energy-demand-tesla-powerpack?redirect=no
[39] | Electrek. Tesla quietly brings online its massive - biggest in the world - 80 MWh Powerpack station with Southern California Edison, (2017). https://electrek.co/2017/01/23/tesla-mira-loma-powerpack-station-southern-california-edison/
[40] | Tesla. Tesla Powerpack to Enable Large Scale Sustainable Energy to South Australia, (2017). https://www.tesla.com/da_DK/blog/Tesla-powerpack-enable-large-scale-sustainable-energy-south-australia?redirect=no Page
[41] | Energy Storage Association. Frequency Regulation Services and a Firm Wind Product: AES Energy Storage Laurel Mountain Battery Energy Storage, (2018). http://energystorage.org/energy-storage/case-studies/frequency-regulation-services-and-firm-wind-product-aes-energy-storage
[42] | ABB. Battery energy storage system PQpluS, (2018). https://new.abb.com/high-voltage/capacitors/lv/bess-products/PQpluS
[43] | S. Saylors, Philip C. Kjær. Rasmus Lærke. Ancillary Services Provided from Wind Power Plant Augmented with Energy Storage, (2014). https://www.ieee-pes.org/presentations/gm2014/PESGM2014P-000718.pdf
[44] | Bloomberg New Energy Finance. New Energy Outlook 2018, (2018). https://bnef.turtl.co/story/neo2018.pdf?autoprint=true&teaser=true
[45] | CleanTechnica. $100/kWh Tesla Battery Cells This Year, $100/kWh Tesla Battery Packs In 2020¦, (2018). https://cleantechnica.com/2018/06/09/100-kwh-tesla-battery-cells-this-year-100-kwh-tesla-battery-packs-in-2020/
[46] | Wardsauto. Two Tidbits From CES: Better Cybersecurity and Cheaper EV Batteries, (2017). https://www.wardsauto.com/ideaxchange/two-tidbits-ces
[47] | Visualcapitalist. China Leading the Charge for Lithium-Ion Megafactories, (2017) http://www.visualcapitalist.com/china-leading-charge-lithium-ion-megafactories/
[48] | International Renewable Energy Agency. IRENA Battery Storage Report, (2015). http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2015/IRENA_Battery_Storage_report_2015.pdf
[49] | Windpower Engineering & Development. Global battery energy-storage system installed capacity will exceed 14 GW by 2020, (2016). https://www.windpowerengineering.com/business-news-projects/global-battery-energy-storage-system-installed-capacity-will-exceed-14-gw-2020/
[50] | International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[51] | Danish Technological Institute. BESS project Smart grid ready Battery Energy Storage System for future grid, (2017). https://www.energiforskning.dk/sites/energiteknologi.dk/files/slutrapporter/bess_final_report_forskel_10731.pdf
[52] | H. Chen, T.N. Cong, W. Yang, C. Tan, Y. Li, Y. Ding, Progress in electrical energy storage system: A critical review, Prog. Nat. Sci. 19 (2009) 291–312. doi:10.1016/j.pnsc.2008.07.014
[53] | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
[54] | R. Benato, G. Bruno, F. Palone, R.M. Polito, M. Rebolini, Large-scale electrochemical energy storage in high voltage grids: Overview of the Italian experience, Energies. 10 (2017) 1-17. doi:10.3390/en10010108
[55] | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596. doi:10.1016/j.rser.2014.10.011
[56] | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015). https://www.sandia.gov/ess-ssl/publications/SAND2015-1002.pdf